PART 2 – SECTION VII

EMPLOYER’S REQUIREMENTS

Training, Operation Supervision and Maintenance

TABLE OF CONTENTS

11	Training, Operation Supervision and Maintenance	3

11.1	General	3

11.2	Qualifications, Experience and Training	3

11.3	Training of Operational Staff	4

11.3.1	General	4

11.3.2	Training subjects in general	5

11.4	Operation of the Treatment Plant	7

11.4.1	Operating procedures	7

11.4.2	Monitoring, sampling and analyses	7

11.4.3	Records of data	9

11.4.4	Management of consumables	9

11.4.5	Recording of unusual or abnormal situations	10

11.5	Maintenance of the Treatment Plant	10

11.5.1	General	10

11.5.2	Maintenance program	10

11.5.3	Building maintenance	11

11.5.4	Site infrastructural maintenance	11

11.5.5	Lifting mechanisms	11

11.6	Health and Safety	11

11.7	Contractor/ Employer Liaison and Communication	11

11.7.1	Reporting to the Employer	11

11.8	Handing Back	12

# Training, Operation Supervision and Maintenance

## General

As the capacity expansion will be implemented within an existing and operational wastewater treatment facility, the Employer already has an operational team in place. Therefore, the Contractor’s responsibilities related to training, operation, and maintenance shall be carried out in close cooperation with the existing O&M personnel. Rather than establishing a completely new team, the Contractor shall focus on integrating new components into the current operational workflow and enhancing the capacity and technical skills of the existing staff where necessary.

The Contractor shall train the operational staff of the Employer before and during Commissioning period. However, the Contractor shall be overall responsible for management and supervision of operation and maintenance of the wastewater treatment plant (WWTP) commissioning period in such a manner that it ensures the required quality of treated wastewater and sludge as stipulated in the here above Document No:2. Training shall be conducted as described in this section.

As a minimum, the Contractor shall provide the following personnel during the training, operation and maintenance period.

- Plant Manager:	Full time

- Process Engineer	Full time

Plant Manager shall be also a Wastewater Treatment Process Engineer, there is no need to assign an additional engineer and just the Plant Manager. However, if necessary or required, any other expert or engineer (i.e. mechanical, SCADA expert) shall be provided by the Contractor. Appointments of these additional experts will not exceed 2 man-months during Commissioning.

The management of the wastewater treatment plant shall be carried out in an efficient and cost-effective manner in accordance with the requirements described hereunder.

Consumables, and electricity shall be paid by the Employer after issuing of the Completion Certificate during the Commissioning Period.

## Qualifications, Experience and Training

The Contractor's personnel shall be suitably qualified and have an appropriate level of training and experience in the operation and maintenance of municipal wastewater treatment plants. The skills to be provided shall be in the areas of, but not confined to:

- Operational management

- Maintenance management

- Wastewater treatment plant operation

- Analytical chemistry

- Plant and equipment maintenance

- Instrumentation and telemetry operation and maintenance

- Administration

- Quality systems implementation and management

- Health and safety planning and auditing.

## Training of Operational Staff

### General

The Contractor shall be responsible for ensuring that the operation and maintenance personnel acquire the skills necessary to operate, maintain service and repair all equipment at the wastewater treatment plant. The Contractor shall also be responsible for ensuring that the operation and maintenance personnel acquire full knowledge of the use of the Operation and Maintenance Manuals.

The Contractor shall prepare a training plan for the approval of the Project Manager and submit it to the Project Manager at least one month before the intended start of the first training course. The plan shall contain an outline of the courses, duration, subjects to be taught, documentation to be issued, names and qualifications of instructors etc.at least one month before the intended

The overall purpose of the training is to enhance the existing staff’s knowledge, skills, and competencies required to operate, maintain, service, and repair all equipment at the wastewater treatment plant, especially with respect to the newly added systems and upgraded units.

- Understand the wastewater and sludge treatment processes

- Operate equipment in an optimal way,

- Improve energy efficiency of the overall plant

- Use the WWTP dynamic modeling software for plant optimization

- Assess the analyses required for biological treatment performance monitoring

- Carry out the necessary adjustments and corrections,

- Undertake correct preventive and normal maintenance,

- Undertake trouble-shooting and repair of all equipment and auxiliaries installed,

- Adjust all equipment to optimize the plant,

- Operate and understand the SCADA system,

- Select the necessary spare parts,

- Intervene in case of disturbance, and

- Understand environmental aspects in relation to smell, safety, ergonomic working positions etc.

All equipment and manuals needed for the training shall be provided by the Contractor and handed over to the Project Manager before commencement of the training.

Personnel having an expert knowledge of the subjects shall undertake the training. Instruction and demonstration shall be given at appropriate levels for skilled and semi-skilled personnel and for plant operators and their supervisors. Separate courses for different categories of staff shall be necessary dependent on number of staff to be trained.

The training shall be given in the Turkish language, if necessary, by use of interpreters provided by the Contractor. Documentation of the training carried out shall be submitted to the Project Manager immediately after the Commissioning.

The Contractor shall provide all the necessary training materials and audiovisual aid, inter alia notes, diagrams, films and other training aid, in order to give the possibility to employees to start the self-education retraining courses and to train the shift employees.

The draft training program, short summary of the materials’ content and the samples of training materials, as well as CVs of the trainers foreseen shall be included in the submission form. The program provided in the submission form shall include, but not be limited to, the following:

### Training subjects in general

The subjects shall be treated theoretically and practically. Emphasis shall be given on practical exercises, which shall occupy at least fifty (50) percent of the training time.

The practical exercises shall include normal maintenance activities, adjustments, use of tools and measuring equipment included in the plant.

Process:

The following disciplines shall be included in the training:

- Basic process design of the WWTP

- Principles of basic unit processes

- Principles of process optimization

- Process trouble shooting.

- Laboratory operation for biological treatment performance analysis

Mechanical Operation:

The following disciplines shall be included in the training:

- Basic principles of mechanical components of WWTP (screens, pumps, blowers, mixers, boilers, sludge dewatering, conveyors etc.)

- Capacities

- Maintenance works

- Tuning in the plant for the optimum performance,

- Basic fault finding and remedy of simple/typical faults

- Reading and understanding the Operation and Maintenance Manuals

- Spare parts

- Safety

- Exercises, practical and theoretical

Electrical Operation

The following disciplines shall be included in the training:

- Switchboards including control equipment (frequency converters, controllers, instruments etc.)

- Basic principles of electrical components (relays, motor starters, ELCBs, etc.)

- Basic fault finding and remedy of simple/typical faults (reset of MCBs etc.)

- Basic principles and operation of the Combined Heat and Power unit (if proposed)

- Maintenance routines

- Detection and remedy of typical faults

- Reading and understanding of diagrams

- Spare parts

- Safety

- Exercises, practical and theoretical.

Training Courses

Theoretical courses are assumed to be carried out separately for each staff category, i.e. laboratory, electricians and operators. Practical courses shall be for both categories.

For each course, a compendium including program, details on the subjects, manuals, exercises (practical and theoretical) shall be prepared. The compendiums shall be submitted to the Project Manager for his approval at least fourteen (14) days prior to the start of the particular training course.

The number of approved compendiums to be issued is two to the Project Manager and one for each of the trainees. Furthermore, the Contractor shall have completed the draft version of the Operating and Maintenance Manuals before the first course.

1st Training Course –Theoretical Introduction

Timing:	Before on-the-job training

Subjects:

- General layout of the plant

- Principles of function of the major components of the plant

- Methods of operating the plant

- Capacities of the plant

- Unit processes

- Process optimisation

- Check routines

- Operation and maintenance

- Occupational health and safety.

2nd Course – On-the-Job Training

Timing:	During the running-in period.

Subjects:

- Acquaintance with the plant

- Participation in the running-in

- Fault finding

- Automatic and manual operation

- Maintenance requirements

- Safety precautions.

3rd Course – Understanding of the Operating and Maintenance Instructions

Timing:	During the running-in period (preferably parallel with 2nd Course)

Subjects:

- Theoretical fault-finding procedures

- Operation and maintenance

- Process trouble shooting

- Ordering of spare parts

- Ordering of consumables

- Checking on capacity of plant

- Checking on all performance parameters.

4th Course – Re-training

Timing:	Approximately 3 months after the 2nd and 3rd Courses.

Subjects:	Repetition of all previous subjects with emphasis on subjects wanted by the Project Manager.

Duration of Training

It is proposed that each of the specified courses shall have duration of minimum three (3) days, apart from the “On-the Job” training course together with 3rd Course, which shall have the same duration as the running-in period.

Training Location

Training shall take place at the Erbaa Wastewater Treatment Plant.

## Operation of the Treatment Plant

Upon issuance of the Completion Certificate, the Contractor shall supervise the operation of the treatment plant using the personnel specified in Section 11.1.

The Contractor shall take full responsibility for the operation of the complete treatment works including all plants and associated services (all civil, mechanical, electrical, telemetry and infrastructural items specified in the Contract), on a continuous basis (24 hours).

### Operating procedures

The Contractor shall provide a detailed procedure for the operation of the wastewater treatment plant. A detailed control philosophy shall be provided for each process stage and it shall be accompanied by a procedure for each individual item of plant. The operating manuals for the wastewater treatment plant shall be used in the development of the operating procedures.

During the operational period the Contractor shall manage together with the Employer staff inspections at regular intervals and maintenance works as described in the Operation and Maintenance Manuals, The Contractor shall also direct, supervise and monitor the Employer’s staff for proper operation of the plants.

### Monitoring, sampling and analyses

General

The Contractor shall carry out monitoring, sampling and analysis of the wastewater and sludge as specified in the herewith Employer's Requirements, Document No 2: Design Basis

Analyses that are capable of being carried out with the analytical equipment provided under the Contract shall be performed at the plant by the operational staff. All other analyses shall be carried out by a recognized independent laboratory, as agreed with the Employer. In this regard, the Contractor shall prepare a plan and submit for approval to the Project Manager.

The Contractor shall carry out monitoring, sampling and analysis in accordance with all relevant regulations in force in Türkiye and with the relevant EU regulations.

The Contractor shall ensure that all on site analysis is carried out in a safe manner and that all waste chemicals and containers are disposed of in a proper fashion.

Sampling Equipment

Automatic flow proportional samplers shall be required as defined in the herewith Employer’s Requirements.

The Contractor shall ensure that all samplers, including sample bottles and pipelines, are cleaned regularly to avoid the formation of grease, solid material and bacterial growth.

Laboratory and Analytical Equipment

The Contractor shall ensure that the laboratory and analytical equipment is kept in good condition. Analytical equipment shall be calibrated on a regular basis.

Analytical Methodology

The Contractor shall also abide by the requirements of the Turkish Regulations with respect to analytical methodology.

In cases where there are no applicable Turkish regulations, the analysis of samples taken at the wastewater treatment plant shall be carried out in accordance with the most up to date edition of “Standard Methods for the Examination of Water and Wastewater” produced by The American Public Health Association (APHA); the American Water Works Association (AWWA) and the Water Environment Federation (WEF).

Monitoring Requirements

For compliance purposes, the Contractor shall carry out sampling according to Table 11 given below. Sampling at the inlet and outlet shall be corresponding as regard time.

Independent Analysis

Analyses for all parameters, specified in Table 11 for the inlet and outlet, shall be carried out at the Plant’s Laboratory. All other analyses that cannot be carried out at plant’s laboratory and the analyses to be required by the Project Manager due any reason shall be carried out by a recognized independent laboratory, approved by the Project Manager. A portion of the sample sent for independent analysis shall be kept on site and analyzed as normal. The results shall then be compared. Any unusual variance between the results shall be brought to the attention of the Project Manager for discussion. The Contractor shall make any necessary adjustments to his analytical procedures to ensure that any errors, considered to have occurred, shall be eliminated.

Remedy on Compliance Failure

In the event of any failure to comply with the treated wastewater discharge standards, the Contractor shall inform the Project Manager, in writing, immediately upon becoming aware of the failure. The Contractor shall provide details of the reasons for failure and the remedies that have been put into effect to ensure that the treatment plant can meet the standards.

Sampling by the Employer

The Employer reserves the right to enter the wastewater treatment plant to take samples at any location and at any time without prior notice to the Contractor.

### Records of data

Records of the continuous data measured at the station shall be kept at the wastewater treatment plant in electronic and hard copy formats and summary data shall be provided in the monthly report.

Table 11	Monitoring Program

| Location | Unit | Inlet | Outlet | Activated Sludge Tank | Return Sludge | Excess Sludge | Dewatered Sludge | Dried Sludge |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flow | m3/day | Con | Con | Con | Con | Con | Calculated | Calculated |
| Temperature | 0C | Daily | Daily | Daily |  |  |  |  |
| pH | s.u. | Daily | Daily | Daily |  |  |  |  |
| Parameters |  |  |  |  |  |  |  |  |
| COD | mg/l | Daily | Daily |  |  |  |  |  |
| BOD5 | mg/l | Reg / FPS | Reg/FPS |  |  |  |  |  |
| SS | mg/l | Daily | Daily | Daily / GS | Daily / GS | Daily / GS | Daily / GS | Daily / GS |
| Total - N | mg/l | Reg / FPS | Daily |  |  |  |  |  |
| Ammonia N | mg/l | Reg / FPS | Reg / FPS |  |  |  |  |  |
| Nitrate N | mg/l | Reg / FPS | Reg / FPS |  |  |  |  |  |
| Phosphate P | mg/l | Daily | Daily |  |  |  |  |  |
| Oxygen | mg/l |  | Daily | Con |  |  |  |  |
| SVI | ml/g |  |  | Daily / GS |  |  |  |  |
| TS | % |  |  |  |  |  | Daily / GS | Daily / GS |

Legend

Con	Continuous
Day	Daily
Reg	Every 10th calendar day
FPS	Flow proportional 24-hour sample
TPS	Time proportional 24-hour sample
GS	Grab sample.

Index
DW	When dewatering unit in operation.

DR 	When drying unit in operation.

### Management of consumables

Chemicals Management

The Contractor shall keep records of all chemicals used for the treatment of wastewater or sludge. The Contractor shall put procedures in place to ensure that the treatment processes are optimized, to minimize the use of chemicals.

Energy Management

The Contractor shall keep records of the hours of operation of each item of electrical plant and the total energy usage of the treatment plant. The Contractor shall put procedures in place to ensure that the treatment processes are optimized, to minimize the energy consumption.

### Recording of unusual or abnormal situations

Unusual circumstances arising from industrial disputes, accidental spillage, mechanical breakdown, power failure, stoppage for essential maintenance or abnormal weather conditions shall be noted by the Contractor in detail and taken into consideration when interpreting the analytical data from the treatment plant.

The Contractor shall notify the Employer of any unusual occurrence or incident in respect of the provision of the Operation and Maintenance Works. Notification shall be made by telephone with immediate effect and shall be followed by a written report of the occurrence or incident.

## Maintenance of the Treatment Plant

### General

The Contractor shall provide for the routine, planned, breakdown and repair maintenance of all assets relating to civil, mechanical, electrical and electronic plant, equipment and infrastructure at the wastewater treatment plant.

Maintenance includes measures taken in order to avoid failure of the plants and equipment in addition to repair measures in case of failure.

### Maintenance program

The Database software for maintenance program to be put in place by the Contractor shall be based on a recognized maintenance methodology. The Contractor shall provide a statement of the methodology he proposes to adapt to the Employer for approval, before developing it in detail.

The maintenance regime adopted by the Contractor shall include:

- Schedules for the maintenance of the treatment plant to include but not be limited to:

  - a complete list of the assets to be maintained

  - the frequency and type of routine and planned maintenance for each asset

  - details of the calibration of all instrumentation

  - a listing of all essential spare parts to be carried

- Methods for dealing with breakdown and repair of assets to include:

  - Call out response times for each asset

  - Communication with the Employer when breakdowns occur.

- Procedures for the maintenance of the assets incorporating manufacturer’s instructions

- Methods for the planned replacement of assets at the Wastewater Treatment Plant

- Records of all maintenance carried out at the Wastewater Treatment Plant, to be kept up to date and held electronically and in paper format at the Wastewater Treatment Plant at all times.

The Contractor shall ensure that the wastewater treatment plant is kept in a clean and tidy condition at all times and shall incorporate a cleaning routine in the maintenance schedules.

### Building maintenance

The Contractor shall manage the maintenance of the all buildings, contained within the wastewater treatment plant, to keep it in good repair throughout the term of the Contract including:

- Regular cleaning of all internal areas

- Repair or replacement of internal and external fixtures and fittings when they become damaged

- Cleaning of roof guttering and drainage, windows and doors

- Maintenance of ventilation systems.

The Contractor shall be responsible for the replacement of any part of the buildings that become damaged during the term of the Contract, excluding damage caused by a Force Majeure event.

### Site infrastructural maintenance

The Contractor shall manage the maintenance of all infrastructures within the wastewater treatment plant, to keep it in good condition throughout the term of the Contract including:

- All road and path surfaces

- Gates and fences

- Water supply facilities

- Road and building drainage

- Landscaped and grassed areas.

The Contractor shall be responsible for the replacement of any part of the infrastructure that becomes damaged during the term of the Contract, excluding damage caused by a Force Majeure event.

### Lifting mechanisms

The Contractor shall be responsible for the certification of all mechanical lifting mechanisms used at the wastewater treatment plant and shall ensure that they are in good repair and capable of operating to the required standard at all times. The maintenance required for such mechanisms shall be detailed in the Contractor’s maintenance schedules. Certificates for lifting equipment shall be kept at the wastewater treatment plant as part of the Contractor's maintenance records.

## Health and Safety

The Contractor shall comply with all aspects of current Turkish legislation in force or that subsequently comes into force during the term of the Contract.

The Contractor shall maintain and update the Safety File on an ongoing basis.

## Contractor/ Employer Liaison and Communication

### Reporting to the Employer

The Contractor shall provide the Employer with a monthly report that includes but is not limited to:

- General commentary on the performance of the Plant

- Details of failures, breakdowns and non-routine maintenance

- Tables of analytical data including graphical representations and a discussion of the results

- Records of sludge management and disposal activities

- Details of any complaints

- Schedule of hours run of all operational plants

- Record of any accidents

- Records of chemical and energy usage

- Summary of weather records

- Any other records or information that shall be considered relevant by the Contractor.

The report shall be submitted to the Project Manager, one copy in electronic format and three copies in paper format, within the first 14 days of each month following the month covered in the Report.

The Employer shall be requesting information, relating to the operation and maintenance of the Plant, from the Contractor at any stage during the Operation and Maintenance Period.

## Handing Back

At the date of expiration of the defects liability period, the Contractor shall hand back the wastewater treatment plant to the Employer for the future operation and maintenance.

The plant shall be in good and maintained condition and the buildings and external works shall be well maintained.

As a guideline, the Contractor shall prior to the handing back ensure that:

- All mechanical and electrical equipment and installations are well-functioning and well-maintained

- All metal parts are free from rust and/or oxide

- Any damage to tarmac and paved surfaces has been repaired

- The treatment plant site is tidy and green areas well gardened

- Rooms in buildings and structures are tidy up and cleaned.

The inspection shall be conducted jointly by the Employer and the Contractor with the presence of Project Manager to arbitrate in the event of disagreement.