PART 2 – SECTION VII

EMPLOYER’S REQUIREMENTS

Design Basis

TABLE OF CONTENTS

ABBREVIATIONS	2

2	Design Basis	4

2.1	General	4

2.2	Hydraulic Loads and Hydraulic Profile	5

2.2.1	Hydraulic Loads	5

2.2.2	Hydraulic Profile	6

2.3	Pollutant Loads	6

2.4	Wastewater Temperature	7

2.5	Effluent Quality and Control	7

2.5.1	Treated Effluent Quality	7

2.5.2	Treated Sludge Quality	8

2.6	Other Environmental Requirements	8

2.6.1	Noise	8

2.6.2	Odour	8

2.6.3	Vibration	9

2.7	Design Lifetime	9

2.8	Directives, Norms and Standards	10

2.8.1	EU Directives	10

2.8.2	International standards and norms	10

2.8.3	CE marking	11

2.8.4	Installations in explosive atmospheres	11

ABBREVIATIONS

| ATEX | Atmospheres Explosibles |
| --- | --- |
| BOD5 | Biochemical Oxygen Demand for 5 days |
| CA | Contracting Authority |
| CB | Circuit Breaker |
| COD | Chemical Oxygen Demand |
| DMS | Document Management System |
| DNP | Defects Notification Period |
| DS | Dry Solids |
| DSİ (SHW) | State Hydraulic Works |
| EC | European Commission |
| EIA | Environmental Impact Assessment |
| ESIA | Environmental and Social Impact Assessment |
| EMC | Electromagnetic Compatibility |
| EMP | Environmental Management Plan |
| EU | European Union |
| EUD | Delegation of the European Union to Turkey |
| FDD | Final Design Deliverables |
| FDR | Final Design Report |
| FIDIC | International Federation of Consulting Engineers |
| GRP | Glass Reinforced Plastic |
| HDPE | High Density Polyethylene |
| ISO | International Organization for Standardization |
| MLSS | Mixed Liquor Suspended Solids |
| MoM | Minutes of Meeting |
| OPEX | One Year Operation Cost |
| ORP | Oxygen Reduction Potential |
| OS | Operating Structure |
| PDD | Preliminary Design Deliverables |
| PDR | Preliminary Design Report |
| PE | Polyelectrolyte |
| PID | Piping and Instrumentation Diagram |
| PIU | Project Implementation Unit |
| PLC | Programmable Logic Controller |
| PP | Polypropylene |
| PPRC | Polypropylene Random Copolymer |
| PSC | Project Steering Committee |
| PVC | Polyvinyl Chloride |
| QA | Quality Assurance |
| RAS | Return Activated Sludge |
| SCADA | Supervisory Control and Data Acquisition |
| SOR | Standard Oxygen Requirements |
| SOTE | Standard Oxygen Transfer Efficiency |
| SS | Suspended Solids |
| SSOTE | Standard Specific Oxygen Transfer Efficiency |
| T.R. | Republic of Turkey |
| TEDAŞ | Turkish Electricity Distribution Corporation |
| TN | Total Nitrogen |
| TP | Total Phosphorus |
| TSS | Total Suspended Solids |
| UV | Ultraviolet |
| WB | World Bank |
| WAS | Waste Activated Sludge |
| WWTP | Wastewater Treatment Plant |

# Design Basis

## General

The Erbaa Wastewater Treatment Plant Capacity Expansion Project will be constructed in two stages. The existing plant is categorized as Stage 1. The second stage, which is the subject of these Tender Documents, is planned to satisfy the estimated wastewater treatment needs of Erbaa Municipality service area up to 2039. The treatment plant will be extended later to satisfy the treatment needs up to 2054 (Stage 3). The design parameters for the Erbaa Wastewater Treatment Plant are set out below.

Process design of the wastewater treatment plant shall be designed according to EN or other international standards. The contractor should use related design standard values.

The plant shall be designed to minimize operation and maintenance activities by using required design criteria and minimum number of units/equipment/instruments as detailed in the following pages of the Employer’s Requirements, ensuring the required process performance.

Summary of works to be executed under this project is stated in the below table.

Table 2.1	Summary of works to be executed under this project

| Main Units | Construction Requirements | Electromechanical Equipment Supply & Installation Requirements |
| --- | --- | --- |
| Inlet Chamber and Overflow Structure | Stage 3 | Stage 3 |
| Coarse Screens | Stage 3 | Stage 3 |
| Inlet Pumping Station | Stage 3 | Stage 3 |
| Fine Screens | Stage 3 | Stage 3 |
| Aerated Grit and Grease Removal Tanks and Sampling Unit | Stage 3 | Stage 3 |
| Blower Station for Grit and Grease Removal Tanks | Stage 3 | Stage 3 |
| Distribution and Collection Chambers | Stage 3 | Stage 3 |
| Anaerobic Biophosphour Tanks | Stage 3 | Stage 3 |
| Aeration Tanks | Existing | All instruments and equipment shall be renovated |
| Aeration Tanks | Stage 2 | Stage 2 |
| Blowers Station for Aeration Tanks | Stage 3 | Stage 2 |
| Final Clarifier Tanks | Existing | All instruments and equipment shall be renovated |
| Final Clarifier Tanks | Stage 2 | Stage 2 |
| Discharge pipeline | Stage 3 | Stage 3 |
| Dewatering Building (Mechanical Sludge Dewatering units) | Existing | Stage 3 |
| Return and Excess Sludge Pumping Station | Stage 3 | Stage 2 |
| Supernatant Water Pumping Station | Stage 3 | Stage 2 |
| Solar Drying Unit | Stage 3 | Stage 3 |
| Effluent Discharge Chamber and Remote Monitoring System | Stage 3 | Stage 3 |
| Main drainage pit and drainage discharge system | Stage 2 | Stage 2 |
| Odour Removal Unit | Stage 3 | Stage 3 |
| Transformer and Generator Building | Stage 3 | Stage 3 |
| Flow Measurement (inlet, overflow, excess sludge, effluent etc.) and Sampling Units | Stage 3 | Stage 3 |
| Potable water storage tanks for potable water system and firefighting system | Stage 3 | Stage 3 |
| Service water storage tank for treated wastewater reuse and landscaping purposes | Stage 3 | Stage 3 |
| Main Pipes Between Treatment Units | Stage 3 | Stage 3 |

The design works shall include full process, architectural, layouts, site piping, mechanical, electrical and automation disciplines to cover Stage 3 requirements.

The Stage 3 units shall be so designed that all units and equipment of all stages shall work in a combination and interconnected units shall minimize impact of single unit failure.

Provision for adding the units and equipment in Stage 2 and Stage 3 shall be incorporated in each and every design discipline i.e., layout, piping and electromechanical equipment of the first stage of the wastewater treatment plant where necessary.

The implementation design of the works will be subject to the approval of the Project Manager.

## Hydraulic Loads and Hydraulic Profile

The design of the wastewater treatment plant shall be based on the wastewater flows and pollutant loads listed in The hydraulic flow rates used for design are given in Table 2.2.

Table 2.2 and Table 2.3 below:

### Hydraulic Loads

The hydraulic flow rates used for design are given in Table 2.2.

Table 2.2	Hydraulic design flow rates

|  | Unit | 2039 Stage 2 | 2054 Stage 3 |
| --- | --- | --- | --- |
| Daily average | m3/day | 17,460.0 | 23,280.0 |
| Minimum (Q37) | m3/sa | 350.27 | 434.59 |
| Average (Q24)-Qavg | m3/sa | 727.50 | 970.00 |
| Design flow (Q16)-QDWF | m3/sa | 1,372.50 | 1,905.00 |
| Maximum (Q12)- QWWF | m3/sa | 1,696.50 | 2,307.00 |

### Hydraulic Profile

The hydraulic profile of the wastewater treatment system shall allow minimum head loss and energy consumption.

Hydraulic design of the wastewater treatment plant should be carried out for the worst-case scenario i.e., for the maximum flow rate of Stage 3 and when one unit is out of operation. The calculations should also be controlled under the minimum flow rate of Stage 2 (i.e., under the control philosophy of the inlet pump) and the maximum flow rate of Stage 2. Even in worst case scenario, equal flow distribution to each treatment unit shall be provided but flooded weirs shall not be designed. Treated wastewater will be discharged to Kelkit river by using existing discharge pipeline with 800 mm diameter.

Hydraulic design of the extension project shall be based on the following structure and water level

- Inlet pipe diameter and elevation: 800 mm and 227.50 m

- Final sedimentation tank weir elevation: 233.34 m

- Discharge elevation to Kelkit stream: 800 mm and 227.65 m

The drawings provided in the tender dossiers are for informational purpose only.

## Pollutant Loads

The estimated pollutant loads at the inlet to the wastewater treatment plant are given in Table 2.3. The values are for the raw water inlet concentrations from the collector lines and include no additional hydraulic and organic loads from the in-plant recycling streams. The design of the treatment plant shall be based on the calculated loads including the recycle streams.

In-plant Recycling Stream Flows and Loads

The flow rate of in-plant recycling streams shall be min. 3% of daily average flow rate, pollutant loads shall be min. 5% of pollutant loads in Table 2.3. Pollutant removal in preliminary treatment units (i.e., screens end grit chambers) shall not be accepted.

Table 2.3	Pollutant loads

| Parameter | Unit | Stage 2 2039 | Stage 3 2054 |
| --- | --- | --- | --- |
| Chemical Oxygen Demand, COD | kg/day | 9,603 | 12,804 |
| Biological Oxygen Demand, BOD5 | kg/day | 4,365 | 5,820 |
| Suspended Solids, SS | kg/day | 5,238 | 6,984 |
| Total-Nitrogen, T-N | kg/day | 1,048 | 1,397 |
| Total-phosphorus T-P | kg/day | 140 | 186 |

## Wastewater Temperature

The wastewater treatment plant shall be designed for a minimum temperature in the process tanks of 12oC. The oxygen demand calculations shall be designed for a maximum temperature of 25oC in the biological tanks.

## Effluent Quality and Control

### Treated Effluent Quality

The wastewater treatment plant shall be designed and constructed to comply with the discharge effluent criteria set out in EU Urban Wastewater Treatment Directive (91/271/EEC), By-Law on Turkish Water Pollution Control , By-Law on Urban Wastewater Treatment and By-Law on Identifying Sensitive Water Bodies and Areas Affecting These Bodies and Improving Water Quality.

The following treated wastewater quality standards are to be met:

Table 2.4	Treated effluent quality

| Parameter | Discharge criteria (outlet)1 | Minimum Removal Efficiency4 % |
| --- | --- | --- |
| BOD5, mg/l | 25 | 70-90 |
| COD, mg/l | 125 | 75 |
| TSS, mg/l | 35 | 90 |
| Total N, mg/l | 101 | 70-80 |
| Total P, mg/l | 1 | 80 |

1. This criterion shall be applicable for the temperatures of the wastewater ≥12 oC

The required treated effluent quality to be fulfilled is in Table 2.4 above. The verification of this fulfillment shall be carried out during the Commissioning Period following the issuance of the Completion Certificate.

### Treated Sludge Quality

The sludge from the wastewater treatment plant will be disposed of in compliance with the By-Law on Use of Domestic and Urban Sewage Sludge in Soil.

The required dry solids content of the dewatered sludge is set out in Table 2.5.

Table 2.5	Treated sludge quality

| Parameter | Criteria |
| --- | --- |
| Dry solid content, DS% of |  |
| Dewatered sludge prior to drying process | 22% |
| Dried sludge | ≥ 80% |
| Reduction in E. coli numbers | ≥99% (2 log10) |

The control of the sludge quality shall be based on grab sampling. The required dry solids content of sludge is set out in Table 2-5 above. The verification of this fulfillment shall be carried out during the Commissioning Period following the issuance of the Completion Certificate.

## Other Environmental Requirements

The wastewater treatment plant shall fulfil the requirements in the Environmental Impact Assessment Report. Environmentally friendly materials and equipment shall be used to the greatest possible extent in the wastewater treatment plant.

The wastewater treatment plant shall fulfil the following additional environmental requirements.

### Noise

The maximum acceptable noise levels are given in Table 2.6.

Table 2.6	Maximum acceptable noise levels

|  | Daytime 08:00 hrs to 20:00 hrs | Night time 20:00 hrs to 08:00 hrs |
| --- | --- | --- |
| Along the fence surrounding the wastewater treatment plant | 50 dB(A) | 40 dB(A) |

All necessary measures to mitigate noise, if it is above the specified limits, shall be taken. These measures include planting of trees, covering of equipment etc.

The verification of noise level fulfillment shall be carried out during the Commissioning Period following the Completion Certificate.

### Odour

The following acceptance criteria shall be applied for odour control in WWTP in following table.

Table 2-7	Odour acceptance criteria

| Parameter | Unit | Criteria |
| --- | --- | --- |
| Removal of hydrogen sulphide | % | 99% |
| Removal of ammonia | % | 95% |
| Odour Value | OU | 1000 |

The verification of the odour treatment fulfillment shall be carried out during the Commissioning Period following the issuance of the Completion Certificate.

### Vibration

The vibration levels of the equipment should be such that these limits are met:

- For hand-arm vibration:

- the daily exposure limit value standardized to an eight-hour reference period shall be 5 m/s2;

- the daily exposure action value standardized to an eight-hour reference period shall be 2.5 m/s2.

- For whole-body vibration:

- the daily exposure limit value standardized to an eight-hour reference period shall be 1.15 m/s2 or, at the choice of the Member State concerned, a vibration dose value of 21 m/s1.75

- the daily exposure action value standardized to an eight-hour reference period shall be 0,5 m/s2 or, at the choice of the Member State concerned, a vibration dose value of 9.1 m/s1.75.

- Workers’ exposure to vibration shall be assessed or measured as specified in 2002/44/EC.

## Design Lifetime

The wastewater treatment plant shall be designed so the various components have lifetimes as set out below. These lifetimes shall apply for 24 hours continuous operation per day and also for discontinuous operation under all local climatic conditions:

- Concrete structures	: 40 years

- Steel constructions	: 40 years (based on application of periodical maintenance)

- Pipes	: 40 years

- Mechanical equipment	: 15 years

- Cables	: 15 years

- Electrical equipment	: 15 years

- Process control equipment,

  - Programmable Logic Controllers	: 10 years

  - Personal Computers	: 5 years

- Instrumentation	: 10 years.

## Directives, Norms and Standards

The Contract shall be executed in compliance with the directives and international standards and norms listed below and all other directives and international standards and norms referred to in other parts of these Tender Documents. For all standards, the updated latest versions shall be used.

The requirements of Turkish Standards (TS) and other Turkish regulations shall be applied if they require higher standards or specify higher quality than the Employer's Requirement or the standards referred to.

Any standard, which fulfils the same functionality and describes the same quality level or better, can replace any of the mentioned standards.

The project site, designated for the construction of a wastewater treatment plant (WWTP), is located within the “DD-2 Earthquake Ground Motion” zone as defined by the Turkish Building Earthquake Code (TBEC 2018). DD-2 corresponds to the design basis earthquake, which has a 10% probability of exceedance in 50 years and an approximate return period of 475 years. As the facility constitutes critical infrastructure, all structural and seismic design works related to the construction of the WWTP shall comply with the applicable requirements of TBEC 2018 for DD-2 level ground motions Standards stated in further sections of this specification are valid for design, supply, construction and installation unless otherwise directed. Upon availability of similar standards for the same subject, the priority of the standards shall be:

- TSE

- EN

- BS

- DIN

- EMC

- IEC

- AGMA

### EU Directives

Directive 97/23/EC on the approximation of the laws of the Member States about pressure equipment

Directive 2006/42/EC on machinery

Directive 2006/95/EC on the harmonization of the laws of Member States relating to electrical equipment designed for use within certain voltage limits

Directive 2004/108/EC on the approximation of the laws of the Member States relating to electromagnetic compatibility and repealing Directive 89/336/EEC

Directive 94/9/EC on the approximation of the laws of the Member States about equipment and protective systems intended for potentially explosive atmospheres

Directive 1999/92/EC on minimum requirements for improving the safety and health protection of workers potentially at risk from explosive atmospheres.

### International standards and norms

EN 14121-1 Safety of machinery - Risk assessment - Part 1: Principles

EN 12100 Safety of machinery - Basic concepts, general principles for design

EN 13850 Safety of machinery - Emergency stop - Principles for design

EN 60204-1 Safety of machinery. Electrical equipment of machines. General requirements

EN 14122 Safety of machinery. Permanent means of access to machinery

EN 61000 Electromagnetic compatibility

EN 12255 Wastewater treatment plants.

IEC 60073 Basic and Safety Principles for Man-Machine Interface, Marking and Identification - Coding Principles for Indicators and Actuators

IEC 60439 Low-voltage switchgear and control gear assemblies

IEC 60947 Low-voltage switchgear and control gear

IEC 60255 Measuring relays and protection equipment

IEC 61131 Programmable logic controllers

IEC 61082 Preparation of documents used in electrotechnology

IEC 60617 Graphical symbols for diagrams

IEC 60076 Power transformers

IEC 60364 Low-voltage installations

IEC 61024 Protection of structures against lightning.

### CE marking

The total installation and all parts of the plant shall be CE-marked under the Machinery Directive and related directives, norms and standards.

The CE marking shall include all required tasks as described in the directive included but not limited to:

- Technical dossiers

- Risk Assessments

- Declaration of conformities.

### Installations in explosive atmospheres

All localities at the treatment plant shall be classified in EX zones under the local laws, the ATEX Directive and other related directives, norms and standards. The Contractor shall have the classification approved by the local authorities. The Contractor shall obtain an ATEX Report from authorized accredited institutions.

The design and the installation shall be carried out under the ATEX Directive and the approved classification. All components shall be selected under the ATEX Directive.

Entered into force upon being published in the Official Gazette, dated 31 December 2004 and no 25687

Entered into force upon being published in the Official Gazette dated 8 January 2006 and no 26047

Entered into force upon being published in the Official Gazette No.29927 dated 23.12.2016

Official Gazette Date: 03.08.2010 Official Gazette No: 27661