PART 2 – SECTION VII

EMPLOYER’S REQUIREMENTS

Plant Description

TABLE OF CONTENTS

ABBREVIATIONS	7

3	Plant Description	9

3.1	Layout Considerations	9

3.2	Process Requirements	10

3.2.1	General	10

3.2.2	Description of required treatment processes	11

3.2.3	Flow measurements	12

3.2.4	Sampling	12

3.2.5	Laboratory and analytical equipment	13

3.3	Plant Requirements	15

3.3.1	General	15

3.3.2	Utilities and main access road	16

3.3.3	Main wastewater collector	16

3.3.4	Wastewater Treatment Plant Units	16

3.3.4.1	Inlet and Overflow Structure 	16

3.3.4.2	Coarse Screens	17

3.3.4.3	Fine Screens	18

3.3.4.4	Inlet Pumping Station	19

3.3.4.5	Aerated Grit and Grease Removal Tanks	20

3.3.4.6	Distribution Chamber for Anaerobic Bio-phosphorus Tanks	22

3.3.4.7	Anaerobic Bio-phosphorus Tanks:	23

3.3.4.8	Chemical Phosphorous Precipitation	24

3.3.4.9	Distribution Chamber for Activated Sludge Tanks	25

3.3.4.10	Activated Sludge Tanks 	25

3.3.4.11	Distribution Chamber for Secondary Clarifiers	26

3.3.4.12	Secondary Clarifiers 	27

3.3.4.13	Treated effluent discharge main and outfall structure	28

3.3.4.14	Blowers for Aeration	28

3.3.4.15	Return and Excess sludge pumping station	29

3.3.4.16	Flow Measurement	31

3.3.4.17	Potable water system	31

3.3.4.18	Dewatering building	33

3.3.4.19	Sludge Drying Units	34

3.3.4.20	Supernatant Pumping Station	37

3.3.4.21	Odour Removal Unit (Bio-Filter)	37

3.3.4.22	Drainage of the Units	39

3.3.4.23	Valve Chambers, Pumping Stations and Pipe galleries	40

3.3.5	SCADA system	42

3.3.6	Measurement and Instrumentation	42

3.3.7	A WWTP Kinetic Modelling Software	43

3.3.8	Emergency diesel generator	44

3.3.9	Architectural design	44

3.3.9.1	Administration Building 	44

3.3.9.2	Transformer and Generator Buildings	45

3.3.9.3	Building for Blowers (Grit and Grease Removal Tank and Activated Sludge Tank)	46

3.3.9.4	Building for Screen and Inlet Pumping Station	46

3.3.10	Heating and Ventilation	49

3.3.11	Pipe Materials	50

ABBREVIATIONS

| ATEX | Atmospheres Explosibles |
| --- | --- |
| BOD5 | Biochemical Oxygen Demand for 5 days |
| CA | Contracting Authority |
| CB | Circuit Breaker |
| COD | Chemical Oxygen Demand |
| DMS | Document Management System |
| DNP | Defects Notification Period |
| DS | Dry Solids |
| DSİ (SHW) | State Hydraulic Works |
| EC | Europen Commission |
| EIA | Environmental Impact Assessment |
| ESIA | Environmental and Social Impact Assessment |
| EMC | Electromagnetic Compatibility |
| EMP | Environmental Management Plan |
| EU | European Union |
| EUD | Delegation of the European Union to Turkey |
| FDD | Final Design Deliverables |
| FDR | Final Design Report |
| FIDIC | International Federation of Consulting Engineers |
| GRP | Glass Reinforced Plastic |
| HDPE | High Density Polyethylene |
| ISO | International Organization for Standardization |
| MLSS | Mixed Liquor Suspended Solids |
| MoM | Minutes of Meeting |
| OPEX | One Year Operation Cost |
| ORP | Oxygen Reduction Potential |
| OS | Operating Structure |
| PDD | Preliminary Design Deliverables |
| PDR | Preliminary Design Report |
| PE | Polyelectrolyte |
| PID | Piping and Instrumentation Diagram |
| PIU | Project Implementation Unit |
| PLC | Programmable Logic Controller |
| PP | Polypropylene |
| PPRC | Polypropylene Random Copolymer |
| PSC | Project Steering Committee |
| PVC | Polyvinyl Chloride |
| QA | Quality Assurance |
| RAS | Return Activated Sludge |
| SCADA | Supervisory Control and Data Acquisition |
| SOR | Standard Oxygen Requirements |
| SOTE | Standard Oxygen Transfer Efficiency |
| SS | Suspended Solids |
| SSOTE | Standard Specific Oxygen Transfer Efficiency |
| T.R. | Republic of Turkey |
| TEDAŞ | Turkish Electricity Distribution Corporation |
| TN | Total Nitrogen |
| TP | Total Phosphorus |
| TSS | Total Suspended Solids |
| UV | Ultraviolet |
| WB | World Bank |
| WAS | Waste Activated Sludge |
| WWTP | Wastewater Treatment Plant |

# Plant Description

## Layout Considerations

A conceptual design of the proposed wastewater treatment plant is presented in Volume 5. This layout is given just for information purpose. The layout to be implemented by the Contractor shall be the responsibility of him. The bidder is free to design and location of all units targeting the optimization of the construction and operational works.

In order to increase stability and work safety in this area, geotechnical precautions such as jet grouting, deep soil mixing, ground nails, retaining walls, shotcrete, etc. will be taken by the contractor if required by the geotechnical survey.

The methodology of excavation and the geotechnical precautions shall be subject to the Project Manager’s approval. The Contractor shall prepare the plant units excavation application projects and geotechnical projects stated the methodology on how to make unit excavations and preparation of required excavation. These projects shall be subject to the Project Manager’s approval.

Tanks and other process structures shall be constructed under the hydraulic profile avoiding any unnecessary pumping. Pipes shall either be buried or located inside buildings and tanks or be arranged in a way that does not disfigure the desired neutral appearance of the plant. To the extent possible, all equipment shall be installed in buildings for aesthetical reasons and to reduce noise to a minimum. Specific requirements for structures, buildings, architecture and landscaping are also given in the Employer’s Requirements, “Building Works” (Document No 9) and “Roads, Landscaping and Fences” (Document No 10).

The layout of the plant shall be logical and feasible, reducing the extent of piping and facilitating the access to the main equipment. The area requirement shall be kept low. There shall be easy access for trucks to all buildings for maintenance and to all containers. The most critical mechanical equipment such as inlet pumps, all sludge pumps, blowers, mechanical decanters etc. shall all have a stand-by unit to be taken into operation in case of breakdown, maintenance or repair.

The new administration building shall be located in such a way that major parts of the plant, including traffic through the main entrance gate, shall be visible from the control room. The administration building shall be constructed including staff facilities, laboratory, control room, meeting rooms etc. . For the operational simplicity, all buildings shall be located in one area.

Coarse and fine screens, inlet pumps and intermediate pumps (if it is proposed), blowers, sludge dewatering equipment other sludge pump stations, etc. shall be installed in separate ventilated buildings that ensure the work safety. The noise levels from ventilators as well as air intake and outlet openings shall not exceed the levels set out in “Design Basis” (Document No 2).

The fences and gates proposed by the Contractor shall be under the specifications in “Roads, Landscaping and Fences” (Document No 10).

The wastewater treatment plant shall be planned and designed to satisfy the needs in Stage 3, in parallel with the requirements defined in “Design Basis” Document No 2. There shall be a possibility of taking one treatment stream out of operation for maintenance and repair.

A surface water drainage system shall be constructed to ensure proper drainage of the entire WWTP site during periods of rainfall. The surface water will be discharged into Kelkit river by gravity flow.

In addition, the layout shall be carefully developed in a way that allows integration of the new treatment units while minimizing disruptions to the ongoing operation of the existing plant. The existing 2 Aeration Tanks, 2 Final Settling Tanks and Sludge Dewatering Building shall be protected in the plant to be completed within the scope of work to be commissioned by the Contractor. Other structures listed in Document 1 (1.2. Scope of the Works) shall be demolished within the scope of the works. All demolition works shall be carried out based on the continuation of the operation of the existing plant. Therefore, construction works shall be planned and carried out in stages, ensuring that any unavoidable interruptions in operation are minimized in both duration and impact. Bidders shall propose a detailed Commissioning and Phasing Methodology with their proposal. This methodology shall be clearly presented in the Work Plan and shall describe transitional phases, mitigation measures, and how operational continuity will be maintained.

## Process Requirements

### General

The design shall be in accordance with the specifications included in this Volume and shall comply with the Urban Waste Water Directive 91/271 EEC, By-Law on Urban Wastewater Treatment  and all relevant EU and Turkish Regulations relevant standards, and other relevant documentation forming part of the Contract.

The Contractor shall be responsible for preparation of implementation design that shall meet the Employer’s Requirements and the performance criteria. Approval of the design and/or acceptance of Contractor’s offer during the tendering stage do not relieve Contractor any of its duties and/or responsibilities to comply with the Contract Conditions and Employer’s Requirements.

In order to treat the wastewater to the required quality, the Contractor shall include, but not be limited to, the following wastewater treatment processes:

- Preliminary mechanical treatment

- Biological treatment using the activated sludge process with nitrogen and phosphorus removal

- Sludge dewatering and drying systems,

The process equipment shall be designed to enable the operators to readily determine and adjust, as necessary, the level of oxygen provided, the return sludge rate etc.

The process of Erbaa Wastewater Treatment Plant shall be nitrification-denitrification process (simultaneous, pre-anoxic zone, post-anoxic zone or step feed) in the activated sludge tanks. This process will be based on carbon, nitrogen and phosphorus removal. After treatment the treated wastewater shall be discharged through the new discharge pipeline.

### Description of required treatment processes

The required wastewater treatment plant shall, as a minimum, include the treatment units listed below. The Drawings, included in Volume 5, shall only be considered as the conceptual design for the plant, where the main, but not all components, are indicated. For example, not all distribution units, valve chambers, collection tanks, mechanical and electrical equipment, bypasses, instruments etc. are shown on the Drawings. It is the Contractor's responsibility to prepare the full final process, architectural and implementation design of the plant.

The minimum requirements in the scope of the proposal are:

- An inlet manhole at the border of the WWTP (Connection from the existing collector to the inlet manhole should also be included)

- Inlet chamber including overflow structure and sampling unit

- Coarse screens, conveyors and containers

- Fine screens, conveyors, screen press and containers

- Inlet pumps

- Inlet flow measurement

- Grit and grease removal tanks with grit classifier

- Blower building for grit and grease removal blowers

- Distribution chamber for anaerobic tanks

- Anaerobic biophosphorus tanks

- Distribution chamber for activated sludge tanks

- Activated sludge tanks

- Blower building for aeration blowers

- Distribution chamber for secondary clarifiers

- Secondary clarifiers

- Effluent flow measurement chamber and remote monitoring system

- Overflow and bypass lines system

- Overflow and bypass line flow measurements

- Treated effluent discharge pipeline to Keltkit River

- Main drainage pit and drainage discharge system

- Odor Removal unit

- Return sludge pumps

- Excess sludge pumps

- Flow measurement for return sludge and excess sludge

- Supernatant pumps

- Polyelectrolyte storage and dosing facilities

- Sludge dewatering units

- Solar Sludge drying units

- Administration building

- Transformers

- Emergency diesel generator set

- Treated wastewater system and landscaping water system

- Potable water system

- Firefighting water system

- Potable water storage tanks for potable water system and firefighting system

- Service water storage tank for treated wastewater reuse and landscaping purposes

The proposed process should comply with the approved Environmental Impact Assessment (EIA) report. It is the Contractor's responsibility to obey all instructions and mitigation measures in the EIA report during the planning and construction phase or to prepare revisions of the EIA report (in case of any non-compliance) in accordance with the pertinent legislation to be approved by the relevant authorities.

### Flow measurements

The following flows shall be continuously measured and monitored:

- Inlet flow (upstream of grit grease removal tank)

- Bypass lines

- Effluent flow (downstream of effluent discharge manhole)

- Return sludge flow

- Excess sludge flow

- Sludge flow feeding dewatering facilities

- Poly dose

- Air flow for grit and grease removal tanks

- Air flow for each aeration tank

For sludge line flow measurement, the flow measurement equipments shall be installed downstream of the pumps.

All bypassed and overflowed wastewater to the receiving body should be measured for the wastewater flow.

### Sampling

Arrangements for sampling shall be provided at the following locations, as a minimum:

- At the inlet to the biological treatment units (anaerobic tanks)

- At the effluent outlet.

Sampling of wastewater and treated effluent at the various locations listed above shall be carried out with automatic (flow proportional and time controlled) composite sampling units. The samples shall be refrigerated. The complete sampling equipment shall be included in the Contract.

In relation to the current legislation, “Real Time Remote Monitoring Station” at the outlet of wastewater treatment plants shall also be supplied and installed by the Contractor within this Contract. Relevant permits, applications, official and administrative correspondences shall be carried out by the End Recipient.

The Contractor shall ensure that all sampling points in the wastewater treatment plant have an open section with suitable safe access to allow the taking of grab samples.

Sampling points for grab samples shall be provided at appropriate places in the sludge pumping and dewatering installations.

### Laboratory and analytical equipment

The Contractor shall provide laboratory facilities for the analysis of the wastewater. The laboratory shall be equipped with analytical instruments, furnishings and equipment necessary for carrying out the testing of wastewater and sludge samples taken at the plant. The laboratory shall, as a minimum, be capable of carrying out testing of suspended solids, total solids, determination of SVI and microscopic assessments for sludge, COD, BOD5, ammonia-N, nitrate-N, total-N, Ortho-P, total-P, pH, temperature, dissolved oxygen and alkalinity.

As a minimum, the laboratory equipment shall include:

- Emergency Shower With Eyes-Washing

- Oxitop 12 Bottles

- 5 pc. Imhoff Vessel with Support

- Bacteria Incubator

- Two sets of BOD Incubator
Working range 20 (+/- 1) °C
Microprocessor controlled
Minimum volume 120 litres

- Drying Oven
Microprocessor controlled
Heating range 50-250 °C (+/- 1)
Minimum volume 120 litres

- Ash Muffle Furnace
Microprocessor controlled
Heating range up to 1100 °C (+/- 1)
Minimum volume 6 litres

- Balances
2 pc. Analytical Balance 
Maximum up to 2000 g and maxımum up to 200 g capacity

- Refrigerator (Class A+)
Internal volume of 370 litres

- Two Magnetic Stirrer
Including heating
Staged adjustment for stirring and temperature

- One Magnetic Stirrer

Without heating

- Three Glass Cylinder (1 Litre)

- Water Distillation Apparatus
Minimum 2 litres per hour capacity

- Vacuum/Pressure Pump
Diaphragm type
Minimum 0.4 bar vacuum, 4 bar pressure capacity
Minimum 2.5 m3/hour capacity

- Desiccator with silica gel

Minimum 18 Liter Volume

- Filtration Apparatus
Triple stainless steel system
Appropriate for 47 mm membrane filter
500 ml stainless steel holding capacity

- Flask heater
Available for 4 boiling flask round bottom
Heat adjustment for each compartment

- Spectrophotometer (for COD, nitrogen and phosphorus components etc.)
Wavelength 400-700 nm, single phototube
Adjustment of wavelength for 5 nm sensitivity
Including 12 glass reading tube

- COD Test Kit (1*25 Unit)

- Nitrate Test Kit (1*25 Unit)

- Nitrite Test Kit (1*25 Unit)

- Ammonia Test Kit (1*25 Unit)

- Nitrogen Test Kit (1*25 Unit)

- Total Phosphorus Test Kit (1*25 Unit)

- Thermo reactor

- Fume Hood

- Two portable pH meters
Range 0-14

- Two Portable oxygen meters
Range 0-10 mg/l

- Two portable SS meters
Range 0-15 g/l

- Two portable conductivity meters

- Kjeldahl Equipment

- Electronic Binocular Microscope

- Coliforms Test Kit

- Three Portable gas detection sensor

- Two Portable complete sampling equipment

- Necessary glassware

- Test kits, reagents, filter papers etc. for monitoring of the treatment plant during the performance demonstration period.

The Contractor shall ensure that the laboratory is fitted with an appropriate ventilation system (independent from administration building) and all other ancillary equipment necessary to ensure a safe working environment for its personnel.

## Plant Requirements

### General

The Contractor shall include, but not be limited to, the following specific requirements.

- The final design of the wastewater treatment plant shall be the full responsibility of the Contractor.

- The Contractor shall apply the wastewater treatment process as described in these Employer's Requirements. The specified numbers of process units, equipment and instruments shall be deemed to be the minimum required numbers.

- Electro-mechanical equipment offered by the Contractor shall be in accordance with the specifications given in Document No 7 and Document No  8. However, during the implementation stage if any equipment which is offered by the Contractor is not covered by the herewith Employer’s Requirements, the Contractor shall supply the specification for the equipment which shall be subject to the approval of the Project Manager.  The energy efficiency of electro-mechanical equipment shall be equal or higher than the first offered electro-mechanical equipment.

- All localities at the treatment plant shall be classified in EX zones in accordance with the local laws, the ATEX Directive and other related directives, norms and standards as per Document No 2 . Hazardous area classification and ex-proof equipment requirement have been defined in the Electrical technical specification Document No 8  (8.4. Hazardous Area Classification and Ex-proof Equipment )

### Utilities and main access road

The Municipality will arrange for the relevant authorities (or by his own facilities) to provide the following utilities up to the boundaries of the Contractor’s responsibility. The boundaries of the utilities within the responsibility of the Contractor are given below. In case of no boundary is defined for any utility or any other interface the coordinates of the interface will be assumed as at the physical boundary of the treatment plant site (fence).

- Access road = the Contractors boundary is the main gate of the wastewater treatment plants site.

- Electrical power = the Contractors boundary is the connection point of transformer to be connected.

- Water supply = the Contractors boundary is at the physical boundary of the wastewater treatment plant site (fence), the exact coordinates shall be defined by the End Recipient.

- Telecom = the Contractors boundary is at the connection of the telecom line to the main telecom switchboard within the plant.

- Internet = the Contractors boundary is at the connection of the Internet to the main server within the plant.

- Natural Gas = the Contractor boundary is at boundary of the wastewater treatment plants site.

- Discharge collector = where the wastewater is discharged directly to the receiving body there is no boundary and the discharge pipeline with all protective covers, manholes and discharge structure are considered within the Contract.

### Main wastewater collector

The existing 800 mm main collector ended at the wastewater treatment plant existing inlet chamber.

The existing collector at last invert pipe elevation is 227,50 m. The contractor shall construct inlet pipe between this manhole and the new inlet structure. The coordinates and levels of the existing manholes are indicative, they shall be measured and verified by the Contractor before design studies.

### Wastewater Treatment Plant Units

#### Inlet and Overflow Structure

The raw wastewater shall come firstly by gravity to the inlet structure from the connection manhole.

Inlet structure shall be designed, constructed and equipped regarding the requirements set in Table 2-1. The maximum flow (QWW,h) of the related stage requirements shall be met for the unit.

Inlet structure shall have minimum two chambers. The first chamber shall be inlet chamber. The other chamber shall have a stone trap unit.

The dimensions of the inlet chamber shall be so determined that this structure shall provide a break in pressure and velocity so as to reduce the energy of incoming wastewater from the main collector. Due to the difference between the inlet water level and effluent discharge water level, the by-pass from the inlet shall not be done.

Inlet structure shall have minimum two chambers. The first chamber shall be inlet chamber. The other chamber shall be bypassing chamber.

The main inlet penstock shall be installedin the inlet chamber. This penstock shall be wall type with double spindle, fully watertight and with electrically driven actuators in accordance with the specifications given in Part 2 –Section VII Document No 7 and 8. The operation status of the penstocks should be monitored and controlled by the SCADA system.

For emergency situations, a bypass line at inlet structure shall be provided and this line shall be connected to treated effluent discharge line. The bypass of the WTTP shall be controlled by means of the weir type penstock. Bypass penstock shall be channel type weir penstock with double spindle and fully watertight. It shall be proportioning and electrically driven actuators. The width of the bypass weir shall be designed and constructed by considering the Stage-3 maximum flow rate. The hydraulic height of the bypass penstock shall be adjusted by considering the Stage-3 maximum flow rate. Therefore, this unit shall not work when this penstock is open, otherwise it shall work as bypass.

Operation of the penstocks in the inlet structure shall be controlled by the ultrasonic level or radar type sensor.

The top of the inlet structure shall also be covered with removable covers and foul air shall be collected from the structure and shall be sent to the odor treatment unit.

#### Coarse Screens

Coarse screens shall remove solids that may be harmful to the inlet pumps.

Coarse screen channels shall be designed, constructed and equipped regarding the requirement set in Document No 2 Table 2-1. The maximum flow (QWW,h) of the related stage requirements shall be met for the unit.

The screens shall be made from stainless steel 1.4404 in order to prevent corrosion.

The cleaning mechanisms of the coarse screens shall be automatically operated by water level sensors (ultrasonic level or radar type sensor)) located upstream and downstream of the screens (level difference). In addition to this, the cleaning mechanisms for the coarse screens shall be operated by time intervals. Time intervals must be adjustable from the SCADA.  Coarse screenings shall be transferred via conveyor and automatically disposed to a container on ground level.

The coarse screens, with their screenings’ containers, shall be located in a building with frost-free conditions. The requirements for the drainage, foul air collection and potable water supply system stated in item 3.3.4.22 and 3.3.4.23 should be met for the building inner area.

The coarse screens shall be locally controlled and operated as autonomous units. The operation status, however, shall be monitored and controlled by the SCADA system. Furthermore, water levels in front of and behind the coarse screens should be monitored from SCADA.

Details of the coarse screens are:

Coarse screens:

Minimum number of coarse screen channel for Stage 3	: 3 channels

Maximum bar aperture	: 30 mm

Type	: automatic screen

Maximum velocity through bars at maximum flow	: 1.2 m/s (in the case of 30% clogging)

Minimum storage capacity and type container	: in accordance with Part 2 –Section VII Document No 7 and 8.

Minimum number of the containers	: 2 items

#### Fine Screens

After passing through the coarse screen channels, the wastewater shall come to the fine screen channels inlet. The distribution channels shall be designed and constructed before, after and between each screen groups, i.e. between coarse and fine screen groups. The aim of this construction is to maintain the cross-operation flexibility of all screens.

Fine screen channels shall be designed, constructed and equipped regarding the requirement set in Table 2-1. The maximum flow (QWW,h) of the related stage requirements shall be met for the unit.

The fine screen shall be of the perforated plate type step screen. The unit may be provided with integrated washing and pressing facility. The screens shall be designed for lifting/tipping out of the channel for service with an overhead travelling crane.

The fine screenings shall be automatically removed, washed, dewatered and transferred to containers. If separate dewatering system is offered, the screenings shall be discharged onto screenings conveyors, which convey the screenings to a washing and pressing system. The screening press proposed by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7. The screening press and perforated screens shall be cleaned with hot water (minimum 600C). The screen building shall contain one squatting wastewater closet, one urinal bowl and one sink.

The screens shall be made from stainless steel 1.4404 in order to prevent corrosion.

The cleaning mechanisms of the fine screens shall be automatically operated by water level sensors (ultrasonic level or radar type sensor)) located upstream and downstream of the screens (level difference). In addition to this, the cleaning mechanisms for the fine screens shall be operated by time intervals. Time intervals must be adjustable from the SCADA.

An area to be used for container station with sufficient service water taps shall be provided for handling and washing the containers. Water used for cleaning purposes of containers shall be properly gathered from the bottom drainage pipe and should be conveyed to the inlet pumping station.

The fine screens, with their screening containers, screening press and conveyors shall be located in a building with frost-free conditions. The requirements for the drainage, foul air collection and clean water supply system stated in item 3.3.4.22 and 3.3.4.23 should be met for the building inner area.

The fine screens shall be locally controlled and operate as autonomous units. The operation status, however, should be monitored and controlled by the SCADA system. Furthermore, water levels in front of and behind the fine screens should be monitored from SCADA.

Details of the fine screens are:

Fine screens:

Minimum number of fine screen channel for Stage 3	: 3 channels

Maximum bar aperture	: 6 mm

Maximum velocity through hole at maximum flow	: 1.0 m/s (in the case of 50% clogging)

Minimum storage capacity and type container	: in accordance with Part 2 –Section VII Document No 7.

Minimum number of the containers	: 2 items

#### Inlet Pumping Station

After passing the fine screen channel, the wastewater shall be lifted by the inlet pumps to a level that will allow gravitational flow through the rest of the wastewater treatment plant. If the Contractor prefers, the inlet pumps can also be located between coarse screens and fine screens. In any case, coarse screen, fine screen and inlet pumps shall be in either same building or separate building. The requirements for the drainage, foul air collection and clean water supply system stated in 3.3.4.24 and 3.3.4.25 should be met for the inlet pumping station inner area.

Inlet pumping station shall be designed, constructed and equipped regarding the requirement set in Table 2-1. The maximum flow (QWW,h) of the related stage requirements shall be met for the unit.

In the architectural design of the pumping station, the distance between each pump must be greater than 0.5 meters. The pumping station shall be designed and constructed for wet or dry installed submersible pumps.

Operation of the pumps shall be controlled by the water level controllers (by using (ultrasonic level or radar type sensor)) in the pump sump. The pumps shall operate in an alternating sequence, including the spare pump in order to minimize the wear of the pumps. The inlet pumps shall be locally controlled and operate as autonomous units. The operation status, however, should be monitored and controlled by the SCADA system. The proper location of the pump sump will be made chamfered to prevent waste accumulation and to direct the wastewater towards the pump. The pumping station shall be designed to prevent septic conditions.

The pumps shall be of the centrifugal type and be rated for raw wastewater. Hence, the impellers can be designed either as canal or screw centrifugal types with non-clogging.

Guide bars and automatic couplings shall allow easy service and maintenance of the pumps. A lifting system with overhead travelling crane shall be provided to carry out the maintenance works for pumps.

Foul air shall be collected from the building and shall be sent to the odor treatment unit. The air of the pumping station has to be H2S and CH4 monitored and warning system shall be installed.

Minimum number of pumps for Stage 3	: 3 channels + 1 spare unit (with all equipped)

Type of pumps	: wet or dry installed submersible

Number of stand-by pump	: min. 1 no.

Control of each pump	: by frequency converter

Minimum efficiency	: 70%

#### Aerated Grit and Grease Removal Tanks

After the inlet pumping station or fine screen (as the case may be), the wastewater shall flow to combined aerated grit chambers and grease removal tanks.

Aerated grit and grease removal tanks shall be designed, constructed and equipped regarding the requirements set in Table 2-1. The maximum flow (QWWF) of the related stage requirements shall be met for the unit.

The grit chamber and grease removal tanks shall be constructed as rectangular concrete structures. Length/Width ratio of the grit and grease removal unit shall be minimum 10.

A diffuser system for the creation of coarse bubbles shall be mounted on the wall over the grit hoppers. The diffuser in grit chamber proposed by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7 and No 8. It shall be possible to dismantle the diffusers and remove them for repair.

The blowers for grit removal shall be located in a separate building located adjacent to the grit and grease removal tanks. The blowers shall be speed controlled by means of frequency-converters. One stand-by blower unit shall be provided in the system.

The grit pumps shall be supplied and installed under “Mechanical Works” (Document No 7) and “Electrical Works” (Document No 8).

Each grit and grease removal tank shall have a  bridge . The submersible grit pumps shall be connected to the bridge and move together with the bridge. The pump can be lowered and removed by chains on 1.4404 stainless steel guide rails. The pump shall transfer the grit to the grit accumulation channel by means of stainless-steel pipelines installed on the grit removal bridge. The grit discharged to this channel shall reach to grit classifier then separated from water and the settled grit shall be transported to containers. On the other hand, the retained grease shall be scraped off into a grease collector pit.

The capacity of the grit pump should be selected twice of the calculated requirement. The classifier proposed by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7. The capacity of the grit classifier shall be 20% higher than the total capacity of the grit pumps. The grit classifier equipment shall be with clean water washing. The efficiency of the grit classifier shall be over 90 % for the particles of 0.2 mm and bigger grit size. The grit classifier will have the bottom drainage and the valve and installed in a suitable location in the building. A screw conveyor will transport the settled grit from the grit classifier to a container with a capacity for approximately one week's grit production. Grit classifier, screw conveyor and grit container shall be located in the same building where the fine screens are installed.

The surface scum and floated grease shall be scrapped by a scraper system mounted on the moving bridge that provides collection and transported into a grease collector pit, and then directed to the drum sieve by means of air lifting. Pipework for air lift system shall be stainless steel. The air requiring for air lift application shall be provided from grit and grease removal blowers. When determining the capacity of these blowers, this additional amount should be considered. After the drum sieve, the scum and floating materials shall be transported to screen press and then collected in the containers.

The limiting criteria for surface load in grease removal part is 25 m3/m2h at maximum flow rate (i.e. QWW,h). The width of grease section shall be min 30% of width of grit section. 1/3 of the maximum flow (QWW,h) rate shall be considered for the hydraulic load of the grease channel.

The grease scrapers and grit pumps shall be autonomously, locally timer controlled.

Each grease and grit removal tank shall be isolated by means of the electrical actuated penstocks installed at downstream of each unit. This penstock shall be adjustable according to water level. These outlet penstocks shall be weir type with double spindle and fully watertight. The operation status of the penstocks should be monitored and controlled by the SCADA system.

The drainage pit shall be designed and constructed on the bottom of each grit removal tank. This drainage pit shall be equipped with the drainage valve that is extended spindle and manual operated.

Minimum number of grit&grease removal tank for Stage 3		: 2 tanks

Minimum retention time at maximum flow		: 5 minutes

Minimum storage capacity and type container		: in accordance with Part 2 –Section VII Document No 7

Minimum number of the containers		: 2 items

Minimum number of grit classifiers		: 2 units

No load reduction in screens and grit and grease removal tanks shall be taken into consideration in the design of WWTP units.

#### Distribution Chamber for Anaerobic Bio-phosphorus Tanks

The distribution chamber shall be designed, constructed and equipped regarding the requirements set in Table 2-1.

This distribution chamber shall receive the wastewater from the grit and grease removal tanks and distribute it evenly to the anaerobic bio-phosphorus tank or to the aeration tanks combined with anaerobic section. The structure shall be made of reinforced concrete and shall be equipped with penstocks or appropriate valves. There shall be the penstocks or valves with electric actuator in accordance with the specifications given in Part 2 –Section VII Document No 7 and No 8. The operation status of the penstocks should be monitored and controlled by the SCADA system. Chambers designed and constructed for the needs of Stage 2 should be isolated by an appropriate material/construction assuring the isolation until installation of penstocks proposed for Stage 3.

The location of the return sludge flow shall be selected and designed by the Contractor.

#### Anaerobic Bio-phosphorus Tanks:

Anaerobic tanks shall be provided for biological phosphorus removal.

The microorganisms in the recycled sludge release captured phosphorus inside the body of the sludge when they are exposed to anaerobic conditions.

The anaerobic bio-phosphorus tanks shall be designed, constructed and equipped regarding the requirements set in Table 2-1. The design flow (QDW,h) of the related stage requirements shall be met for the unit.

From the anaerobic bio-phosphorus tanks, the wastewater shall flow to a distribution chamber and shall be distributed evenly to the activated sludge tanks. It shall be possible to operate the anaerobic bio-phosphorus tank and activated sludge tanks separately and to take each tank out of operation for inspection or maintenance.

The tanks shall be constructed as reinforced concrete structures. Each of the anaerobic tanks shall be equipped with submerged energy efficient mixers in order to ensure an efficient mixing of sludge and water and to avoid the settlement of sludge in the tanks. The proposed mixers by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7 and No 8. Each mixer has a separate lifting equipment compliant with Part 2 –Section VII Document No 7 for the hoisting of the mixers. The mixers shall be designed for minimum horizontal velocity of the water of 0.3 m/s. Computational Fluid Dynamic (CFD) analyses for the mixers shall be submitted during the design stage and the mixers will be subject to the approval of the Project Manager.

The tanks shall be equipped with service bridges. The sprinkler system shall be designed and installed along the service bridges to prevent and/or remove the surface scum in the anaerobic bio-phosphorus tanks. The treated water should be used for this purpose. The drainage pit shall be designed and constructed on the bottom of each anaerobic tank. This drainage pit shall be equipped with the drainage valve that is extended spindle and manual operated.

In addition to these, each anaerobic tank shall be equipped with one oxidation reduction potential (ORP) measurement devices, at the outlet of the tank.

The volume of anaerobic biophosphorus tank should not be taken into consideration for sludge age determination.

Minimum number of anaerobic bio-phosphorus tank for Stage 3	: 2 tanks

Minimum contact time at				: 0.75 hour at (QDW,h+QRS) 					  where QRS = 0,75 x QWW,h

#### Chemical Phosphorous Precipitation

Biological phosphorus removal shall be supplemented by chemical phosphorus treatment. The chemical dosing facilities shall be designed for chemical phosphorus removal. The extra sludge quantities shall be taken into account in the design of the sludge treatment facilities.

Chemical phosphorus removal shall be carried out by simultaneous precipitation of the iron trivalent (40% FeCl3).

The dosing system shall consist of as a minimum;

- storage tanks

- dosing pumps in accordance with Part 2 –Section VII Document No 7

- pulsation damper

- filters

- service water connection

- pipes, valves and accessories

- back pressure valve

- emergency eye shower

- electrically driven mobile pump (chemical resistant) for emptying the bounded area

- potable water connection

Storage Tanks

- material: GRP / HDPE

- type: double skinned (if GRP used)

- level control/gauge

- supply pipe with coupling and overflow pipe

- drain with flange and isolating valve

Chemical storage system and all equipment related to chemical phosphorous precipitation shall be installed inside the existing dewatering building.  The chemical storage area shall have the heating system to prevent the frost conditions. This area including all walls and floor shall be isolated with the material to maintain protection against the adverse effects of the chemical.

These storage tanks shall be placed in the concrete safety tanks. These tanks shall be designed and constructed to prevent the chemical spill. The inner volume of this concrete safety tank shall be %10 higher than the volume of the storage tank. Emergency eye shower shall be installed outside the building and close to the entrance door of this building.

The storage tank coating will be UV resistant and color according to ISO standard for handling of chemicals.

The requirements for dosing pumps are defined in Part 2 –Section VII Document No 7. The properties of dosing pumps shall be selected regarding this safety tank dimensions and level.

The capacity of storage tanks and dosing pumps shall be provided for Stage 3 requirements based on daily average flow and assuming that only biological enhanced phosphorus removal shall take place i.e. additional hi-tech removal will not be taken into account for capacity calculations.

Minimum number of storage tanks	: 2 units

Minimum number of chemical dosing pump	: 1 duty +1 standby unit

Minimum storage capacity of chemicals	: 30 days

#### Distribution Chamber for Activated Sludge Tanks

The distribution chamber shall be designed, constructed and equipped regarding the requirements set in Table 2-1.

This distribution chamber shall receive the wastewater from the anaerobic bio-phosphorus tanks and distribute it evenly to the activated sludge tanks of all stages. The structure shall be made of reinforced concrete. There shall be the penstocks or valves with electric actuator accordance with the specifications given in Part 2 –Section VII Document No 7 and No 8. The operation status of the penstocks should be monitored and controlled by the SCADA system. Chambers designed and constructed for the needs of Stage 3 should be isolated by an appropriate material/construction assuring the isolation until installation of penstocks proposed for Stage 3.

#### Activated Sludge Tanks

The aeration tanks shall be designed, constructed and equipped regarding the requirements set in Table 2-1.

In the aeration tank, biological decomposition of organic matter takes place by means of microorganisms (activated sludge) suspended in the wastewater. The biological processes for decomposition of the organic matter require the supply of considerable quantities of oxygen and mixing. In order to obtain the maximum operational stability and to keep power consumption low, the mixing and the aeration shall be separated. The biological processes continuously create new microorganisms (activated sludge). An equivalent amount of sludge shall be removed from the process tank as biological surplus sludge.

The activated sludge tank shall be designed to allow efficient removal of COD and nitrogen by biological process.

The Contractor shall clearly define the type of denitrification process in his tender he proposes and provide with all the necessary equipment and arrangements in terms of layout, PID, process control devices.

The sludge loss through effluent should not be taken account for the calculation of the excess sludge amount.

The aeration system shall be based on floor-mounted fine bubble aeration diffusers. The diffuser system shall be divided into separate grid sets in order to allow servicing of separate units. Each grid set shall have maximum 5% of the total diffuser number of one aeration tank. The anoxic zones, which are required for denitrification, shall be created by the manipulation of aeration within the reactor by dissolved oxygen set point and additional ORP control and NO3 analyzers by the SCADA system.

An adequate amount of the compensators and sliding supports and/or brackets shall be supplied to meet the enlargement of the aeration pipes.

Each of the aeration tanks shall be equipped with submerged energy efficient mixers in order to ensure the efficient mixing of sludge and water and to avoid settling of sludge in the tanks. Each mixer shall  has a separate lifting equipment compliant with Part 2 –Section VII Document No 7 for the hoisting of the mixers.  The proposed mixers by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7. The mixers shall be designed for minimum horizontal velocity of the water of 0.3 m/s. Computational Fluid Dynamic (CFD) analyses for the mixers shall be submitted during the design stage and the mixers will be subject to the approval of the Project Manager.

Aeration shall be automatically regulated by air control valve with electric actuator as per Part 2 –Section VII Document No 7 installed for each aeration tank, based on measurement of the oxygen concentration in the individual tanks. If simultaneous denitrification shall be proposed, each tank shall be equipped with two oxygen measurement devices and transmitters (one oxygen probe in anoxic zone and one in aerobic zone). The output of the blowers for aeration shall be automatically controlled in correspondence with the actual oxygen concentration in the activated sludge tanks.

Flow meters (pitot tube or other reliable type) should be installed on each air pipes to aeration tanks individually.

The tanks shall be fitted with service bridges and shall be designed for easy emptying.  Width of each service bridge shall be minimum 120 cm excluding the air pipes and balusters. Air pipe network on the aeration tanks shall be so designed that easy access to whole instrumentation shall not be hindered.  Each tank can be disabled for individual maintenance if division is required. The drainage pit shall be designed and constructed on the bottom of each aeration tank. This drainage pit shall be equipped with the drainage valve that is extended spindle and manual operated.

Minimum number of activated sludge tanks for Stage 2	: 3 tanks

Minimum number of aeration tanks to be constructed in

the scope	: 1 Tank

Minimum number of oxygen meters for each tank	: 2 units (1 for oxic and 1 for anoxic zone)

Minimum number of ORP meters for each tank	: 2 units (for anoxic zone)

Minimum number of NO3 analyzers	: 1 unit

Maximum dimensioning MLSS concentration	: 4000 mg/l

The sprinkler system shall be designed and installed along the service bridges to prevent and/or remove the surface scum in the aeration tanks. The treated water should be used for this purposes.

#### Distribution Chamber for Secondary Clarifiers

The distribution chamber shall be designed, constructed and equipped regarding the requirements set in Table 2-1.

This distribution chamber shall receive the wastewater from the activated sludge tanks and distribute it evenly to the secondary clarifiers to be constructed. The structure shall be made of reinforced concrete. There shall be the penstocks or valves with electric actuator accordance with the specifications given in Part 2 –Section VII Document No 7. The operation status of the penstocks should be monitored and controlled by the SCADA system. Chambers designed and constructed for the needs of Stage 3 should be isolated by an appropriate material/construction assuring the isolation until installation of penstocks proposed for Stage 2.

#### Secondary Clarifiers

The secondary clarifiers shall be designed, constructed and equipped regarding the requirements set in Table 2-1.

The activated sludge liquor shall be collected from the activated sludge tanks and distributed into the secondary clarifiers. In the clarifiers, suspended sludge and treated wastewater shall be separated by sedimentation. The treated wastewater shall be drawn from the surface by overflow weirs and the settled sludge shall be concentrated in the bottom hoppers. The concentrated sludge shall be returned to the activated sludge tanks in order to secure a sufficient quantity of activated sludge in the tanks. The return sludge pumping shall be proportional to the flow measured by the inlet flow meter. The surface scraper moving on the whole surface of the tank shall ensure collection and transport of floating sludge via screw conveyer system or chain track system or any other system which can remove floating materials by force. Surface scum and floating materials shall be removed from the tanks and should be conveyed to the return sludge pumping station.

The clarifiers shall be constructed as circular tanks with their bases either flat or sloping towards hoppers located in the center of the tanks.

Wastewater from the activated sludge shall gravitate to the clarifiers and shall be distributed into the tanks. The weir channels shall be constructed along the perimeter or sidewalls.

Each clarifier tank shall have a separate moveable bridge. The bridge collector mechanisms shall be sludge the scraper type with center well in the circular tanks or hopper well in the rectangular tanks. The scraper mechanisms will be configured to fully sweep the clarifier slab with each trip. All elements belong to clarifier mechanism that are below the water line shall be stainless steel 1.4404.

Center drives shall be provided with a torque indicator, and furnished with a mechanical disengagement mechanism, whenever the rotating assembly is jammed.

The clarifiers shall be fitted with V-notch overflow weirs and scum boards and floating scum funnels shall be installed. The removed scum shall be collected in a scum pit for pumping to the sludge storage tank.

Minimum number of secondary clarifier tanks for Stage 2		: 3 tanks

Minimum number of secondary clarifier tanks to be

contructed in the scope		: 1 Tank

Minimum return sludge at maximum flow		: 0.75·QWW,h

Surface hydraulic load at maximum flow		:  1.6 m3/m2.hour for QWW,h

Sludge thickening time		:  2.0 hour

Sludge volume loading rate qSV		: ≤ 500 l/(m2·h)

#### Treated effluent discharge main and outfall structure

The treated effluent from the plant shall be discharged to the receiving body through the new discharge pipeline after an effluent discharge flowmeter chamber. This effluent discharge manhole on the treated effluent main to combine all discharge and bypass lines from the WWTP units, if it is possible.

The outfall structure shall be designed by the Contractor and shall be submitted to approving the Project Manager.

#### Blowers for Aeration

The power distribution panel and MCCs for blowers shall be placed in a different room other than the blowers. Number of blowers shall be determined in such a way that minimum each blower serves one aeration tank. In addition to this, one stand by blower shall be provided.

The oxygen and air requirements of biological process during the Stage 3 of operation (2054) shall be considered in determination of capacity of blowers. The blowers shall be located close to the activated sludge tanks in a building to protect the equipment against the weather conditions and to protect the environment against the noise generated by the blowers.

The aeration equipment capacities shall be in such amount to keep the minimum oxygen concentration in the aeration tanks 2 mg/l. The blower capacity calculation has to be based on internationally accepted design standards or ATV-DVWK-A 131E Standard (German Association for Water Pollution Control).

The blowers shall be of the air bearing or magnetic bearing type or integrally geared centrifugal type with servo operated variable diffusers and servo-operated variable pre-rotation systems for maximum efficiency. All blowers will be equipped with motor, frequency converter, air inlet filter, support, accosting hood, non-return valve and flexible discharge connection, safety valve and pressure gauge. Individual blower shall be switched “ON/OFF”, in case of blower failure and also in order to equalize hours of operation, hours of individual blower an automatic changeover “Duty/Standby” shall be provided.   At each blower discharge pipeline, isolating valve shall be provided. Type of valves must be suitable for air applications.  In order to discharge the compressed air between the non-return (check) valve and blower, a blow off valve and its pipeline shall be installed on outlet of each blower. Type of blow off valve shall be solenoid, pneumatic or actuator controlled. There shall be a thermometer and a manometer on common pressure pipeline of blowers. These instruments shall be controlled and monitored by the SCADA system. The blowers and auxiliaries proposed by the Contractor shall be in accordance with the specifications given in Part 2 –Section VII Document No 7.

The blowers shall be supplied with silencer hoods or cabinet. The maximum acceptable noise level in the blower room shall be maximum 85 dB. The maximum acceptable noise levels in WWTP are given in Table 2.6 (Document No.2). Special attention shall be given to the air inlet system, and the temperature in the blower building shall be calculated and necessary measures shall be taken.

The blower room shall be provided with a travelling overhead crane for installation and service requirements.

The blowers shall be autonomous and locally controlled. The set point for the oxygen shall be controlled by the SCADA system which shall also monitor the operation of the blowers.

For the calculation of the blower capacities, the minimum required O2 concentration in the tanks, peak factor for carbon or nitrogen load (whichever the highest), and maximum wastewater temperature, maximum ambient temperature of 45C at 50% relative humidity, water depth, diffuser performance, static head and dynamic friction losses and complete mixing of aerobic zone must be taken into consideration. The performance data of the blower and diffuser shall be submitted together with the tender.

All air piping shall not be buried. All required piping from blower building up to the water level in aeration tank shall be in stainless steel and rest of air pipe shall be HDPE 100 PN 16 considering the external physical impact.

The blower building shall be provided a proper ventilation in accordance with “Heating and Ventilation” section of this document.

#### Return and Excess sludge pumping station

The excess and return sludge pumping station shall be designed, constructed and equipped regarding the requirements set in Table 2-1 (Document No.2).

The pumping station and all equipment shall be located in a building. The requirements for the drainage, foul air collection and clean water supply system stated in Section 3.3.4.24 and 3.3.4.25 should be met for the pumping station inner area.

Return sludge flow measurement shall be a standard in-line flow meter (electromagnetic) for continuous flow monitoring and recording. Easy access to flowmeter for installation, dismantling and maintenance shall be secured and unhindered. For this purpose suitable lifting system shall be provided.

The accuracy of flow measurement device shall be ±0.5 % of the measured flow. The flow measurement device shall have a minimum capacity of 30% higher than maximum (QWW,h) flow of second stage. The measured flow and status of the pumps should be monitored by the SCADA system.

Return sludge pumping station shall consist of separate and independent pump sumps for each secondary clarifier. In addition, one spare pump sump shall be provided. There shall be one pump in each pump sumps including spare pump sump. An ultrasonic level measurement sensor shall be provided for each pump sum including spare pump sump.

Each secondary clarifier tank’s sludge suction pipeline shall be equipped with a suitable electrical actuator valve or penstock at the inlet point of the return sludge pump sump to maintain the separate and simultaneous sludge suction from each tank. Each pump sump shall be connected separately to spare pump sump with a suitable electrical actuator valve or penstock.

Bottom level of pump sum shall be minimum 1.5 m lower than the bottom level of sludge hopper of secondary clarifier to ensure drainage of the secondary clarifier via return sludge pump.  Return sludge line between the secondary clarifiers and return sludge pump sums shall be inclined towards pump sums with an appropriate slope.

The internal volume of the return and excess sludge pumping station shall be dimensioned to allow access to all instruments and maintenance and repair of the instruments. A lifting system with overhead travelling crane shall be provided to carry out the maintenance works for return and excess sludge pumps.

Adequate space within the unit shall be left for proper operation and maintenance of all equipment. Access to the machines, pumps and components (such as valves and local control panels) shall be secure and unhindered.

Return sludge pumps

The pumps for return sludge shall be submersible pumps with frequency converters. The actual capacity of the pumps shall be regulated automatically based on the inlet flow measured and a selected rate of return of activated sludge. The return rate shall be determined by the required sludge concentration in the activated sludge tanks.

The total installed capacity of return sludge pumps shall be minimum 100% x QWW,h without using the standby unit.

The pumps shall be of the centrifugal type and be rated for return sludge. Hence, the impellers shall be designed either as canal or screw centrifugal types.

The measured flow and status of the pumps should be monitored by the SCADA system.

Excess sludge pumps

The pumps for excess sludge shall be submersible pumps or eccentric screw pump. The pumps shall be speed controlled by means of frequency-converters. Adequate space within the unit shall be left for proper operation and maintenance of all equipment. Access to the machines, pumps and components (such as valves and local control panels) shall be secure and unhindered. Service water connections shall be supplied so that the pump can be washed back on the suction and discharge lines.

Minimum one additional stand-by excess sludge pump shall be provided.

Minimum number of excess sludge pump	: 4 (3 duty +1 standby) units

Design of operation hour of the excess sludge pumps	: 8 hours/day

Washing water shall be connected to both the suction and discharge lines of the sludge pumps. This washing system will engage automatically when the pumps are not operated. In addition, the service water line shall be installed to the appropriate places of the excess sludge pumping station and sufficient number of connection points shall be supplied. The treated water should be used for this purpose.

#### Flow Measurement

##### Inlet Flow Measurement

A standard open channel measurement (ultrasonic) unit or in-line flow meter (electromagnetic) shall be installed downstream of the grit and grease removal tanks for continuous flow monitoring and recording.

Regardless of type, easy access to flow meter for installation, dismantling and maintenance shall be secured and unhindered. In addition to this pH, conductivity and temperature of wastewater shall be measured at this unit.

The accuracy of flow measurement device for electromagnetic type shall be ±0.5 % of the measured flow. The flow measurement device shall have a minimum capacity of 30% higher than the maximum flow of Stage 3.

##### Effluent Flow Measurement

A standard open channel measurement (ultrasonic) unit or in-line flow meter (electromagnetic) shall be installed before outlet structure for continuous flow monitoring and recording. Regardless of type, easy access to flow meter for installation, dismantling and maintenance shall be secured and unhindered. For these purposes suitable lifting system shall be provided.

The accuracy of flow measurement device for electromagnetic type shall be ±0.5 % of the measured flow. The effluent discharge line to receiving body shall have enough capacity to carry at least twice of the maximum flow of second stage. The flow measurement devices on effluent discharge line shall have a minimum capacity of 30% higher than the capacity of the effluent discharge line.

##### Bypass Line Flow Measurements

A standard open channel measurement (ultrasonic) unit or in-line flow meter (electromagnetic) shall be installed for continuous flow monitoring and recording. Regardless of type, easy access to flow meter for installation, dismantling and maintenance shall be secured and unhindered. For these purposes suitable lifting system shall be provided.

The accuracy of flow measurement device for electromagnetic type shall be ±0.5 % of the measured flow. All by-pass lines shall have enough capacity to carry at least twice of the maximum flow of second stage. The flow measurement devices on all bypass lines within the WWTP shall have a minimum capacity of 30% higher than the capacity of by-pass lines.

#### Potable water system

Potable water supplies shall be made available to the Administration Building, the Guard House, workshop, screen building, sludge dewatering building and any other locations as required. Firefighting, polymer preparation and dilution water shall also use potable water. The firefighting system shall be supplied and erected in complete compliance with the relevant Turkish Law and local regulations. The Bidder shall design, supply, install and commission all the necessary pumping and storage systems together with the necessary piping and auxiliary units in complete. In order to control the water level of firefighting water storage tank, a valve with hydraulic floater shall be provided. Storage tanks and all other necessary equipment (e.g. pumps, valves, etc.) for treated wastewater, potable water and firefighting water shall be located in the same building.

#### Dewatering building

The dewatering building shall include centrifuges,  polymer preparation units and other auxiliary equipment used for dewatering. Existing Dewatering Building shall be used for this purpose. All existing equipment will be abandoned, and in-building equipment shall be supplied and installed within this scope. The renovations required for the installation of new equipment in the existing building shall be made and completed within the scope of the work.

The complete dewatering facilities shall be locally and automatically controlled and monitored on the SCADA system. Local control devices and/or panels for dewatering / thickening equipment including a local control center of SCADA system shall be placed in this operation room.

All sludge shall be treated in the dewatering facilities. The sludge shall be pumped by frequency-controlled eccentric screw pumps for sludge feeding. A lifting system with overhead travelling crane shall be provided to carry out the maintenance works of dewatering facilities.

Supernatant from dewatering process(es) shall be delivered back to the system by gravity as possible. The mixture of supernatant with drainage water and sewerage generated in the WWTP is not permitted.

The polymer shall be used for conditioning of the sludge. The polymer shall be prepared in a polymer generation unit. The polymer generation unit shall allow either liquid or powder polymer to be diluted/dissolved to a predefined concentration and automatically mixed and matured. The polymer generation unit shall be a stand-alone unit and shall be automatically controlled locally by a local control panel. The minimum storage capacity of polymer shall be 30 days. The Contractor shall provide the Employer with the details and type of polymer prior to the commissioning of the sludge treatment facilities.

The polymer shall be dosed by means of eccentric screw type pumps controlled by frequency converters.

Washing water shall be connected to both the suction and discharge lines of the polymer dosing pumps and decanter feeding pumps. In addition, the service water line shall be installed to the appropriate places of the sludge thickening and dewatering building and sufficient number of connection points shall be supplied. The treated water should be used for this watering.

Dewatered sludge shall be conveyed by fully closed suitable conveyors equipped with an appropriate drainage system and designed to prevent leakage to a level and a position that allows the sludge to be dumped.

Final destination of the dewatered sludge shall be the solar sludge drying units. Conveyor system shall transfer the dewatered sludge to directly sludge drying facility. However, transfer to one of the containers devoted for dewatered sludge and/or directly to sludge storage area shall also be considered for emergency cases.

In order to remove backwash water that will be generated during backwashing from the system without taking to the conveyor, a suitable hydraulic or pneumatic lid system to decanter’s sludge outlet chute will be built. The compressors required for the decanter will be fixed (not mobile) and the piping will be made according to the criteria specified in the mechanical specification.

Minimum number of centrifuges	: 2 (1 duty + 1 stand-by) units

Maximum daily operation time	:  8	hours/day

Weekly operation time	: 7 days/week

Minimum dry solids content of dewatered sludge	:   22 % DS

Minimum number of polyelectrolyte preparation system	: 1 duty unit

Minimum number polyelectrolyte dosing pumps	: 2 (1 duty + 1 stand-by) units

Capture rate of solids in dewatering                                              : min. 95%

#### Sludge Drying Units

Solar sludge drying unit shall be designed, constructed and equipped to increase the dry solid content, to further sterilize the sludge and to enhance storage capability before final disposal. Solar sludge drying plant shall be installed in turnkey to meet the required sludge output characteristics. Further requirements are given in Part 2 –Section VII Document No 7.

The dewatered sludge shall be dried to get minimum outlet sludge dry solids content of 80%. Please note that dewatered sludge prior to drying process shall be taken as 22% DS as specified in Table 2.5

The solar drying units shall be composed of minimum automated sludge turning/moving equipment and sludge drying hall structures including climate-controlled ventilation system, under floor or other heating systems.

The minimum number of drying halls and turning/moving equipment shall be at least 2. To prevent infiltration, a geo-membrane shall be placed under the drying halls.

Sludge distribution within the drying hall shall be by means of the sludge turning/moving equipment.

In the detailed design of sludge drying facilities in WWTP, the local solar radiation values shall be used and the given solar radiation values shall not be exceeded in calculation of evaporation and heat transfers. For the proposal 1400 Kwh/m2.month raditaion is taken into account but for the detailed design, the contactor shall maintained local radiation from the related authorities

Sludge Drying Halls

Concrete Works: Foundation slab shall be reinforced concrete. In the design of slab, live load shall be taken as min. 10 kN/m2. The surface of concrete shall be flat and smooth.

Steel Works: The steel frames shall be hot dip galvanized St37 steel. All welding shall be completed before the galvanizing and other connections required after galvanizing shall be done with bolts and nuts made of galvanize. The fixing to the concrete shall also be done with steel dowel made of galvanize.

Cover Material: Depending on the snow load and wind load determined for the region in accordance with TS 498 Design Loads for Buildings, double walled polycarbonate material having min. thickness of 8 mm, max. 4.2 W/m2K heat transfer coefficient and min. 80% light transmittance shall be used as cover material. The polycarbonate material shall also be UV protected and dew resistant. Material to be used in sealing shall be solvent free.

Electrical and Controls

The electrical and control works shall include, but not limited to, the following items:

- Supply of all electrical and control elements associated with the Sludge Drying processes (Load in, Turning, load out, and hall environment control including under-floor or other heating if required)

- PLC based control system complete with software.

- Supply of a Motor Control Centre for the Sludge Drying process

- Supply of Equipment instrumentation and all associated cabling.

- Local control stations.

- All ancillary cabling, terminals and other electrical devices associated with the Inlet Works installation.

The Contractor shall provide a PLC based control system that will manage the operation of all the items of Equipment that comprise the Sludge Drying process.

The Contractor shall provide all control panels and instrumentation that are required for the operation and protection of the Sludge Drying process.  The individual elements of the Sludge Drying shall be able to operate in manual and automatic modes.

The control system shall, as a minimum include the following:

- Supply of a complete PLC controller including battery backed power supply, CPU, IO Modules, terminals and local operator control panel.

- Installation of the PLC system in a standalone (Wall mounted or Free Standing) Instrumentation, Control and Automation (ICA) panel.

- Supply of all instrumentation and field control stations

The Contractor shall provide the control software for the PLC control system and operator control panel.

The Contractor shall develop a functional description for the software in accordance with the Control Philosophy. The functional description shall be submitted to the Project Manager for review. This document shall outline the following:

- Operation of equipment in manual and automatic mode

- Description of alarms

- Description of PLC inputs and outputs

- Description of hard-wired protection, interlocks and personnel safety devices.

Each process unit of Sludge Drying Process shall include protective devices to stop the respective process unit in case of the following abnormal conditions. As a minimum these shall include but not be limited to the following:

- Overload of an electrical motor;

- Abnormality of the variable speed drive for a motor.

- All necessary sensing and protection equipment to achieve the required protection for the individual items of equipment and the Sludge Drying facility as a whole.

The Sludge Drying shall generally comprise the following electrical and control equipment:

- Air circulation and extraction system and associated motors and variable speed drives

- Under floor or other heating if required

- Indoor temperature and humidity sensing instrumentation

- Outdoor temperature, humidity, wind speed and wind direction sensing instrumentation

- Load in, load out and disposal conveyors and associated motors, starters and rotation sensors.

- Sludge turning equipment and associated motors, starters and limit switches

- Emergency Stop pushbuttons, pull wires, light beams and the like

- PLC based control system

All process data (e.g. inlet and outlet sludge amounts, electricity consumption, heating values, drainage water flow rates etc.) shall be transferred to SCADA system to monitor and control the sludge drying unit.

#### Supernatant Pumping Station

Supernatant from dewatering and thickening process (es) shall be delivered back to the system by gravity as possible. However, in case gravitational flow is not possible, a supernatant pumping station shall be provided.

All supernatant water shall be collected to the supernatant pumping station. The pumps for supernatant shall be submersible pumps. The actual capacity of the pumps shall be calculated by taking the maximum amount of supernatant water into account. The backwash water of mechanical thickener and decanter shall also take into account in determination of maximum capacity. Ultrasonic level sensors shall be used in pump tanks for pump operation. Supernatant water flow rate shall be measured in accordance with “Measurement and Instrumentation” section of this document.

The mixture of supernatant with drainage water and sewerage generated in the WWTP buildings is not permitted.

The pumps shall be the centrifugal type and be rated for raw wastewater. Hence, the impellers can be designed either as canal or screw centrifugal types. A lifting system shall be provided to carry out the maintenance works.

The discharge point of the supernatant shall be selected and designed by the Contractor.

Minimum number of pumps	: 1 duty + 1 stand-by units

Maximum daily operation time	:  8 hours/day

#### Odour Removal Unit (Bio-Filter)

The wastewater treatment plant shall not cause troublesome odor problems inside or outside the plant. The bidder shall provide detailed calculations (e.g. volume and recycle rate from each potential source) for foul air to be extracted from the sources together with his proposal. Minimum recycle rate and locations foul air to be collected are as follows:

- Screening building (12 cycle/hour)

- Inlet, return, excess and dewatering facilities feeding pumping stations (12 cycle/hour),

- Dewatering building (12 cycle/hour),

In addition to this, the ventilation of these units shall be provided in accordance with item 3.3.10.

In the design of odor units, the average and maximum H2S concentrations in the foul air in the inlet pipe of unit shall be assumed at min. 30 ppmv and min.60 ppmv respectively and units shall be designed accordingly.

The air ductwork dimensions shall be so selected that the minimum velocity in any duct shall not be less than 8 m/s to avoid clogging by settlement of solids. In any case, the air velocity in the duct shall not exceed 12 m/s.

The odour removal system shall include the minimum following items, but not limited to:

- bio-filter bed and bio-media to treat the foul air, which contain H2S, NH3 and similar odorous compounds, to be received from the odor releasing units

- the extractor fan,

- air ductwork between the extractor fan and the odour releasing units,

- a pre-conditioning unit

- sprinkler system for bio-media

- service water and drainage connection for filtrate water from the bio-filter

- (nutrient feed) media preparation and dosing system and necessary instrumentation.

Operation and maintenance manual shall be prepared by the Contractor as well the other equipment. The media to be supplied for the bio-filter shall be commercially available with proper price regarding the media renewal.

The foul air shall be collected with an extractor fan from all the above locations liable to produce significant objectionable odors. The foul air then shall be transferred to the bio-media (bio-filter) bed after passing through the pre-conditioning unit where the heat, moisture and pH values are to be measured. Passing through the bio-media bed, treated air shall eventually be emitted to the atmosphere. In case of malfunctioning of the pre-conditioning unit or for the sake of operational flexibility, the air can directly be transferred to the bio-filter beds after bypassing the pre-conditioning unit. For the start/stop operation, an actuated valve shall be used.

Extractor Fans

- Minimum one duty and one spare fan shall be provided.

- The shaft, all the fasteners, bolts, chassis and supports shall be of EN 1.4404 (316L) stainless steel. Fans shall be statically and dynamically balanced.

- The fan shall be operated with a frequency converter to allow the control of flowrate.

- The fan shall be selected considering an additional head loss of 1000 Pa to the total head loss in piping system and the odour removal unit.

The bidder shall submit the report based on the calculation of the fan's flow rate and pressure class in his tender.

Electrical panel

The panel shall be equipped with the below given components required to control, protect and start up the fan and other instruments, but not limited to:

- PLC process controller

- IP65 protection class

- All required switches, contactors and circuit breakers;

- Overload relay;

- Local ON/OFF buttons for all equipment;

- Warning lights.

- VFD

- UPS just for the panel

Instrumentation

H2S, NH3 monitoring at the outlet of the odour removal unit. Instant measurement and periodic measurement options should be available for these sensors. The measurement ranges of these sensors and the sensor installation point/area shall be subjected to the approval of the Project Manager. All process data of the odor treatment system itself and operating information of equipment and instruments to be installed on this system shall be transferred to SCADA system. Since the toxic gas measurement has a priority for the labor safety, there should be back-up system for these measurements. In addition, the communication system of these sensors should have alternatives such as Ethernet and GSM etc.

Biological process and Bio-media Unit

The Contractor shall design and construct the bio-media unit in line with the design criteria specified above. This unit shall be reinforced concrete. The inner surfaces shall be painted with special epoxy paint against corrosion and aggressive media. Perforated HDPE pipes shall be installed on its floor for the distribution of the collected foul air. The unit shall be filled with bio-media.

Water to be sprayed intermittently on the media bed shall flow downwards in the opposite direction of the foul air flow and the media surface shall keep wet according to bacterial need of media. A drainage system shall be provided to drain the water from the bottom of bio-media bed. The water, once filtered down the media after sprayed intermittently on the media, shall under no circumstances be sprayed on the media again or reused in the media bed.

To provide protection against the atmospheric conditions and allow the inspection of the bio-filter bed, the unit shall be covered with UV resistant, curved elements made of GRP.

Pre-conditioning Unit

A pre-conditioning unit made of HDPE containing PVC filling material and equipped with moisturising nozzles shall be provided and installed.

The unit shall include a circulation pump having a stainless-steel shaft and body together with its standby pumps. Necessary stainless steel EN1.4404 (316L) piping work shall be done. pH adjustment unit shall be equipped with dosage pumps together with its standby pumps. Control equipment consisting of a heater in sufficient capacity together with its accessories, a thermometer, a moisture analyser, a flow meter, a gas analyser, a pressure gauge and a pH meter shall be provided. All necessary control units and panels shall be provided. The bio-media unit shall have a control room for controlling and monitoring purposes

#### Drainage of the Units

The following conditions should be met for the appropriate drainage of the units but not limited to;

- The main drainage pit shall be designed, constructed and equipped to make the gravitational discharge of the tanks possible, i.e aeration tanks, bio-phosphorus tanks and grit and grease removal tanks etc. The depth of this drainage pit shall be designed considering minimum 1.5 m lower than the bottom level of the deepest tanks to be drained. Each tank shall have the bottom drainage and the valve and these are installed in a suitable location of that tank.

The drainage pump capacity shall be so selected that the biggest tank shall be emptied in one day. There shall be one stand by pump. Minimum two discharge lines for pumps shall be provided in the drainage pit. One of these lines shall be directed to the plant discharge line before outlet flow measurement and the other one shall be directed to the inlet of the plant.

- The drainage of the secondary clarifier shall be carried out by means of the return sludge pumping station. For the complete drainage of the final clarifier tanks, the bottom level of the return sludge pumping station shall be 1.5 m lower than the secondary clarifier tank hopper bottom level.

#### Valve Chambers, Pumping Stations and Pipe galleries

For all valve and instrument chambers, pumping stations and pipe galleries;

- Treated water supply system shall be designed and installed with all required equipment, valve, pipe, fittings, etc. for washing and cleaning purposes.

- The floor of these chambers, pumps rooms and these galleries shall be designed and constructed with appropriate slope. There shall be drainage channel at the lowest edge of the chambers and the side of the gallery. At the end of this channel, there shall be the permanent drainage pump readily for use at drainage pit. This drainage pit shall be constructed considering the installation of the drainage pump.

- Foul air shall be collected from the buildings/rooms/galleries and shall be sent to the odor treatment unit. For foul air collection; the collection piping network system with appropriate material shall be designed and installed in the buildings/rooms/galleries. This network shall be designed and installed to collect the foul air from the top and floor part of the areas. The main collection line shall be installed at the top of the rooms with appropriate distance to the ceiling and the foul air at the bottom part shall be collected with the pipe branches (drop legs) connected to this top main collection line network. H2S and CH4 monitoring and warning system shall be installed for the buildings/rooms/galleries. Minimum recycle rate and locations foul air to be collected are given in Document No 2 (2.6.2. Odour)

- If the pumping station shall be designed and constructed as buried, a lifting system shall be provided to carry out the maintenance works.

### SCADA system

A computer-based control and monitoring system (also known as a SCADA system: Supervisory Control and Data Acquisition System) shall be provided for automatic control and monitoring of the treatment plant. All electrical and electronic equipment used in the treatment plant facilities (even if they are packaged units) shall be controlled and monitored with SCADA.

The control and monitor system of SCADA shall include an individual Local Control Center. All data from the local control center shall be transferred to main SCADA system in the Administration Building. The Local Control Center shall be in Sludge Dewatering.

The SCADA system detail and requirement are given in Document No 8.

### Measurement and Instrumentation

Instrumentation shall be provided to enable the required parameters and equipment to be monitored and the plant to be automatically operated and controlled.

The following measurement units shall be provided, but not limited to:

- Inlet pumping station:

  - Ultrasonic or radar level measurement at the pump sump

  - Pressure gauge (manometer) of the submersible pumps

  - Safety measurements for Methane (CH4) and Hydrogen sulphide (H2S) with acoustical and optical alarm at the pump room

- Screening:

  - Ultrasonic or radar level measurement

  - Safety measurements for Methane (CH4) and Hydrogen sulphide (H2S) with acoustical and optical alarm at the screen room

- Influent flow:

  - Flow measurement

  - pH

  - Conductivity and temperature

- Activated sludge tank:

  - Oxygen meter , 2 pcs./1 basin

  - ORP meter, 2 pc. / 1 basin

  - NO3 analyzer, 1pc. / Basin

  - Air flow meter for air pipes, installed within the common supply pipes of the individual basins.

  - Pressure gauges, installed within the common supply pipes of the individual basins.

- Return and Excess PS:

  - Ultrasonic or radar level measurement at the pump sump

  - Magnetic Inductive Flow measurement for return sludge pressure line

  - Magnetic Inductive Flow measurement for excess sludge pressure line

  - Pressure gauges, installed within the common supply pipes of the individual basins.

  - Safety measurements for Methane (CH4) and Hydrogen sulphide (H2S) with acoustical and optical alarm at the pumping station room

- Sludge dewatering:

  - Magnetic Inductive Flow measurement in the polyelectrolyte dosing line

- Supernatant (Filtrate) water pumping station:

  - Ultrasonic level measurement at the pump sump with supplementary low and high level switches

- Effluent flow:

  - Flow measurement

  - pH

  - Temperature

  - Conductivity

### A WWTP Kinetic Modelling Software

The Contractor shall provide commercially available wastewater treatment kinetic modelling software capable of handling at least the processes that will be applied in Erbaa Wastewater Treatment Plant.  This model shall be provided during design preparation stage and be used to verify the Contractor’s design by using design criteria given in the Employers Requirements.

System modeling software shall be original licensed product that was prepared for this purpose. The program should be a commercially and operationally proven program. Excel or other types of reporting software will not be accepted.

The software shall be used for modelling and simulation of the treatment plant. The use of model should provide:

- Process optimization

- Bottleneck identification

- Cost savings caused by optimised operation

- Control strategy evaluation

- Scenario/extreme event evaluation

- Changes in wastewater load/composition

- Automation

The model should be able to cooperate with the SCADA system to collect the relevant process data. The use of model should allow a preventive measure for different situations and scenarios and should give the operators at the WWTP the possibility to adjust operation strategies according to the expected events and even model the effects of a numerous of scenarios that could be taken place.

The awarded contractor shall analyze the raw wastewater, more than once, to measure the kinetic parameters such as fraction of the COD, yield coefficient and other necessary ones. The software shall be used during the execution stage using these parameters to verify the Contractor’s design. Even smaller process volumes and/or less equipment capacities are found during modelling compared to the ones of the Contractor’s design at tendering stage, the bigger volumes and capacities shall be kept as they are to give flexibility during operation.

The WWTP staff should be trained for using, characterization of wastewater and sludge and calibration of the model. The software together with its license, permits etc. shall be property of the End Recipient. The Contractor shall pay all the costs related to providing it and training of the software.

The bidder shall provide software technical specifications together with his tender.

### Emergency diesel generator

An emergency diesel generator shall be provided and shall be in accordance with Document No 8. The capacity of the generator shall be determined by the Contractor based on the %80 of installed capacity of the offered equipment and the required power needs during a mains power failure.

### Architectural design

The buildings shall achieve an architectural unity and follow the local area building traditions and shall form an aesthetic synthesis with the surrounding landscape and, at the same time, shall comply with the local building regulations and the architectural requirements given below. The proposed architectural structure for the administrative building the exterior application of the form shall be submitted for final approval by the beneficiary and the authority. Architectural design shall also be carried out in accordance with the EU visibility principles to reflect the EU visibility.

Buildings shall be designed with either pitched roofs or flat roofs with eaves and membrane protective.

Buildings on more than two levels shall not be accepted.

#### Administration Building

The building shall contain the following facilities and rooms as a minimum (Gross area ≥ 300 m2):

- Entrance hall

- Panel room

- Plant control room including plant operator's office

- Separate office for plant manager

- Separate office for the laboratory manager

- Separate office for administrative staff

- Separate office for technical staff

- Separate office for process staff

- Meeting room

- Cafeteria for the staff

- Kitchen area

- Changing rooms and bathing facilities for the staff

- Laboratory and laboratory chemicals store

- Toilet facilities for man, woman and disabled persons

- Storage rooms equipped with shelves.

The facilities shall be designed for a staffing of approximately twenty persons. All furniture and equipment of buildings shall be brand new.

The minimum height inside the building shall be 2.90 m.

The insulation of the building shall be in accordance with Turkish standards for office buildings. The minimum inside design temperature shall be 24oC.

The building shall be equipped with phone/fax/e-mail connections, projector, writing tables (120*200) for meeting rooms, desk chairs, filing lockers, shelves, desk lamps, tables and chairs in the canteen, refrigeration, cooking and eating facilities, kitchen fittings, service sets for 20 persons etc. necessary for the operation staff. This equipment shall be of a good quality subject to approval by the Project Manager.

Separate air conditioners shall be provided and equipped for each individual room in the administrative building. Devices shall be in compliance with the standards TS 7936 EN 60335-2-40, TS EN 814-3, TS EN 14511-4 and the energy consumption of air conditioners shall be Class A.

There shall be a 1: 250 scale, 3-dimensional illuminated, descriptive (Turkish and English) industrial architectural model of the wastewater treatment plant. The model shall be made from first class materials and subject to the approval of the Project Manager and the Contracting Authority. The model shall be placed at an appropriate location in the entrance hall of the administrative building.

#### Transformer and Generator Buildings

The building layouts shall suit the local authorities' approval.

#### Building for Blowers (Grit and Grease Removal Tank and Activated Sludge Tank)

The internal volume of the blower building shall be dimensioned to allow access to all instruments and maintenance and repair of the instruments. The building shall be provided with a travelling overhead crane for installation and service requirements.

Adequate space within the unit shall be left for proper operation and maintenance of all equipment. Access to the blowers and components (such as valves and local control panels) shall be secure and unhindered.

The buildings shall be provided a proper ventilation in accordance with “Heating and Ventilation” section of this document.

The building shall contain the following items, as a minimum:

- Power panels

- Blowers

- Crane

#### Building for Screen and Inlet Pumping Station

The building shall contain the following items, as a minimum:

- Screens (coarse and fine screen)

- Conveyors

- Containers

- Screen Press

- Grit Classifiers

- Inlet Pumps

- Crane

- Panels

- WC and Sink

### Heating and Ventilation

General

Proper heating and ventilating systems shall be provided in several buildings and units in the wastewater treatment plant.  A boiler system or independent combi boiler for each building shall be used for the heating system. Air conditioners and electrical heaters shall not be used. All buildings shall be heated by either diesel/light fuel or natural gas. In addition air conditioning system shall be provided for Administrative building, guard house and all offices in the other buildings.

The units to be heated:

- Administrative Building		: All locations

- Guard House		: All locations

When the weather is cold, the following temperature values shall be ensured in the buildings:

- Administrative building, guard house, laboratories and control room: 24°C

- Equipment and machinery rooms, pump rooms : 20°C

- Kitchens, stairs, corridors and toilets : 20°C

The Contractor shall provide details of the design study to be carried out for heating and ventilating, including the drawings showing the general arrangement of the proposed layout.

The buildings to be heated shall comply with relevant heat insulation regulations, and the calculations showing in the architectural drawings that the respective average heat transfer coefficient value of windows/external walls has been achieved shall be provided together with heating designs.

In any locations constituted as an enclosed volume such as valve room, pump room, etc., natural circulation shall be provided. To do this, at least 2 windows, etc. opposing to one another shall be placed and insulated against external effects.

Ventilating

Ventilation systems shall provide those buildings:

- Coarse screen and inlet pumping station

- Fine screen

- Blower buildings

- Return and excess sludge pumping station

- Sludge dewatering building

- Laboratory (Separate ventilation apart from Administration Building)

- Dewatering Building

- Transformer Buildings

- Emergency Diesel Generator Building

- Service, Potable and Firefighting Water Pumping Station

Ventilation systems shall provide a safe working environment to comply with national regulations and to the key-principles given in Document No 2 (2.6.2. Odour)

### Pipe Materials

Pipes to be used at the plant;

Connection pipes between units 	: HDPE PE100

Process air pipes 	: Stainless steel 1.4404

Drop legs for process air pipes

Above water	: Stainless steel 1.4404

Below water	: HDPE PE100, PN16

Aeration grid pipework below water	: HDPE PE100, PN16

Odor Pipes	: GRP

Sludge pipes 	: HDPE (section outside the buildings and in underground installation)

Sludge pipes 	: Stainless steel 1.4404 (section inside the buildings)

Discharge, overflow and drainage pipes	: Corrugated PE, Reinforced concrete, box (for pipes with diameter > 1600 mm)

Service water pipes 	: HDPE (PE100) or PPRC

Sewage pipes inside the buildings 	: HDPE PE100

Chemical Lines 	: HDPE, PP

Pipe Velocities

The following flow velocities for each individual media shall be used.

| Media | Velocity |
| --- | --- |
| Wastewater |  |
| Gravity flow | 0.6 m/s at average flow |
| Pressure flow | 2.5 m/s at maximum flow |
| Sludge |  |
| Gravity flow | 0.6 m/s at average flow |
| Pressure flow | 1.8 m/s at maximum flow |
| Compressed air |  |
| for DN > 600 | 12 m/s |
| for DN 300 – DN 600 | 10 m/s |
| for DN 75 – DN 250 | 8 m/s |

Entered into force upon being published in the Official Gazette dated 8 January 2006 and no 26047