PART 2 – SECTION VII

EMPLOYER’S REQUIREMENTS

Mechanical Works

TABLE OF CONTENTS

7	Mechanical Works	5

7.1	General Requirements	5

7.1.1	Suitability of design and equipment	5

7.1.2	Environment	5

7.1.3	Program of works for machinery	5

7.1.4	Coordination	6

7.1.5	On-site manufacturing	6

7.1.6	On-site storage and safekeeping	6

7.1.7	Erection	7

7.1.8	Standards	7

7.1.9	Equipment and manufacture	7

7.1.10	Machinery guards and labelling	8

7.1.11	Lubrication	8

7.2	Corrosion Protection	8

7.2.1	General	8

7.2.2	Galvanizing	9

7.2.3	Painting in particular locations	9

7.2.4	Preparation and painting of steel work	10

7.3	Steel Constructions	11

7.3.1	Structural steel	11

7.3.2	Wrought steel	11

7.3.3	Cast iron	11

7.3.4	Stainless steel	12

7.3.5	Aluminium and aluminium alloys	12

7.4	Welding	12

7.4.1	Welding in general	12

7.4.1.1	Welding Procedure Qualification	13

7.4.1.2	Qualification of Welders and Welding Operations	13

7.4.1.3	Welding of Pipelines	13

7.4.1.4	Welding Preparation	13

7.4.1.5	Welding	13

7.4.1.6	Materials	14

7.4.1.7	Cleaning of Carbon Steel Items after Welding	14

7.4.1.8	Identification of Weld Seams	14

7.4.1.9	General Requirements, Welding Inspection	14

7.4.1.10	Extent of Examination, Welding Inspection	15

7.4.1.11	Acceptance Criteria	15

7.4.1.12	Production Testing	16

7.4.1.13	Document Requirements	16

7.4.1.14	Coating of Weld Seams	16

7.4.2	Welding of carbon steel	16

7.4.3	Welding of stainless steel	17

7.5	Bolts	17

7.5.1	Chemical anchors and anchor bolts	17

7.6	Steel Pipework	18

7.6.1	Pipes from stainless steel	18

7.6.2	Pressure test of pipes	19

7.6.3	Flanges	19

7.6.4	Pipe bends	19

7.6.5	Tapers	20

7.6.6	Flush appliances	20

7.6.7	Branch pipes	20

7.6.8	Measuring instruments	20

7.6.9	Vent pipes	20

7.6.10	Pipe brackets	20

7.6.11	Installation of piping	21

7.7	Stairs, Walkways, Platforms and Handrails	21

7.7.1	Staircases and galleries	21

7.7.2	Access ladders	22

7.7.3	Open mesh and chequer plate flooring	22

7.7.4	Hatches	23

7.8	General Mechanical Equipment	23

7.8.1	Lifting Equipment	23

7.8.1.1.	Slewing davits	23

7.8.1.2.	Jib Crane with electrical	24

7.8.1.3.	Electric Chain Hoist with Monorail	24

7.8.1.4.	Overhead Travelling Cranes	25

7.8.2	Ventilation	26

7.8.3	Drive units	26

7.8.4	Bearings	26

7.8.5	Motors	26

7.8.5.1	General	26

7.8.5.2	Mechanical Requirements	27

7.8.5.3	Electrical Specifications	27

7.8.6	Balancing	28

7.8.7	Suppression of noise	28

7.8.8	Penstocks	28

7.8.9	Gate valves	29

7.8.10	Knife gate valves	30

7.8.11	Non-return valves	30

7.8.12	Butterfly valves	30

7.8.13	Dismantling joints	31

7.8.14	Expansion joints	32

7.8.15	Ball valves	32

7.8.16	Surge anticipating control valves, air relief and vacuum protection valves	32

7.8.16.1	Surge Anticipating Control Valve:	32

7.8.16.2	Pressure Relief Valve:	33

7.8.17	Telescopic valves	33

7.8.18	Electric actuators	34

7.8.19	Pumps	34

7.8.19.1	General	34

7.8.19.2	Submersible pumps for dry installation	35

7.8.19.3	Submersible pumps for wet Installation	36

7.8.19.4	Centrifugal pumps for dry installation	37

7.8.19.5	Progressive cavity pumps (Eccentric screw pump)	38

7.8.19.6	Rotary lobe pumps	39

7.8.19.7	Grit, Grease and Scum Pumps	40

7.8.19.8	Dosing pumps	40

7.8.20	Clamshell Grab Bucket	41

7.8.21	Coarse screens	41

7.8.22	Fine screens	42

7.8.23	Conveyer systems	42

7.8.23.1	Spiral-conveyer	42

7.8.23.2	Belt conveyers	43

7.8.24	Drum Sieve	43

7.8.25	Screenings press	44

7.8.26	Grit and grease removal equipment	44

7.8.27	Diffusers in grit chambers	45

7.8.28	Grit classifier	46

7.8.29	Containers for screenings and grit	46

7.8.30	Submersible mixers	46

7.8.31	Blowers	48

7.8.31.1	Positive Displacement Blowers	48

7.8.31.2	Centrifugal/Turbo Blowers	49

7.8.31.3	Factory Acceptance Test of Centrifugal/Turbo Blower	50

7.8.32	Aeration diffusers for the activated sludge tanks	50

7.8.33	Aeration diffusers for the aerobic digesters	51

7.8.34	Scraper bridges for the clarifiers	51

7.8.35	Effluent troughs, baffles, stengel and scum boards for clarifiers	54

7.8.36	Service bridges for circular tanks	55

7.8.37	Service bridges for process tanks	55

7.8.38	Dewatering equipment - mechanical decanter	57

7.8.38.1	Decanter Centrifuges	57

7.8.39	Polymer preparation and dosing system	58

7.8.40	Sludge Drying Unit	59

7.8.41	Well water supply system	59

7.8.42	Treated wastewater for reuse supply system	60

7.8.43	Spare parts	61

7.8.44	Tools	61

# Mechanical Works

## General Requirements

In the following are outlined the general and particular minimum requirements for mechanical installations at the Erbaa Wastewater Treatment Plant.

It shall be the responsibility of the Contractor to provide all detailed design of the installatiootns, to ensure full coherence of all the equipment installed and to comply with the present minimum quality requirements. If equipment, not mentioned in this section, is offered, the Contractor shall with his Bid demonstrate through submission of documentation and specification that the proposed equipment is of equal or better quality than the requirements to quality specified in this section.

New offered equipment or vehicles shall have a higher energy efficiency and quality than the original offer.

In addition to the requirements set out below, all equipment and mechanical installations to be used at the Erbaa Wastewater Treatment Plant shall comply with occupational health and safety regulations in force, including the requirements specified under the “Regulation on Health and Safety Conditions in the Use of Work Equipment” concerning periodic inspection criteria and intervals. The Contractor shall ensure that all equipment is subject to mandatory inspections within the legally prescribed timelines and shall provide valid inspection certificates prior to site acceptance and testing.

### Suitability of design and equipment

During the selection and/or design of equipment and installations, particular attention shall be paid to the following:

Safety of operation and easy maintenance

Well-proven and reliable components

Ability to withstand the service conditions

Inaccessibility for vermin, dust and humidity

Precautions to minimize corrosion

Spare parts available in Türkiye

Service available in Türkiye

Minimization of noise

Alterations of design and make of the offered equipment after the contract has been signed shall only take place with the consent of the Project Manager.

### Environment

All equipment shall be rated for the ambient temperatures relative humidity and altitude at the Site. Necessary frost protection by means of insulation and, if so required, also electric heat tracing shall be considered in the design.

The Contractor shall in his design and selection of equipment take into consideration under which conditions each item shall be in operation. Equipment placed in the open shall be designed for solar radiation induced temperatures or in some way protected from direct sunlight.

Equipment placed in or near wastewater shall be efficiently protected against the intrusion of humidity and water.

Equipment placed where the risk of condensation prevails shall be provided with drainage holes placed in the lower part of the equipment.

Equipment shall moreover be designed for preventing intrusion of insects and smaller reptiles.

### Program of works for machinery

The program of works for machinery to be supplied and installed shall be divided into the following parts:

Part I	Manufacturing period:

Design and manufacture of all equipment to be supplied under the contract including inspection and works testing.

Part II	Shipping period:

Delivery of all equipment from factory to the Contractor's on site storage including all freight loading, off-loading, customs duties and clearance.

Part III	Erection period:

Removal of the materials and equipment from off or on-site storage, delivery to erection site and installation.

Part IV	Site testing:

All mechanical equipment and machinery shall be subjected to on-site testing in the presence of the Project Manager prior to initial operation. These tests shall confirm that the equipment is installed correctly and operates in accordance with the technical specifications defined in the Contract.Part V	Running-in and Tests on Completion:

All installed mechanical equipment and machinery shall be adjusted and fine-tuned to meet the operational requirements and actual site conditions. The Contractor shall provide operation manuals and other documentation as specified in Employer’s Requirements, Document No. 4: General Requirements for the Execution and Completion of the Works.

Performance testing shall be conducted by an independent accredited body in the presence of both the Project Manager as specified in Employer’s Requirements, Document No. 4: General Requirements for the Execution and Completion of the Works.

### Coordination

It is the responsibility of the Contractor to ensure full coherence between the equipment delivered according to the present mechanical specifications and the specifications for electrical and civil works.

The Contractor shall also be responsible for all sub-contractors and suppliers of equipment and materials. No direct formal communication between the Employer and the sub-contractors shall be permitted.

It is the responsibility of the Contractor to secure that sub-contractor and suppliers get all the relevant information of the present specifications.

The Contractor shall appoint and provide an experienced mechanical and electrical engineer to monitor and co-ordinate all aspects of the mechanical and electrical work.

### On-site manufacturing

It is the obligation of the Contractor to provide all installations within the working area as he considers necessary for on-site manufacturing and shaping of materials and equipment. The working site shall be used as intermediate storage for equipment at the Contractor's own risk and at his own cost.

It shall be noted, that the Contractor's obligations on taking the necessary safety precautions shall apply for the working camp area as well.

### On-site storage and safekeeping

The Project Manager shall be informed by the Contractor about machinery delivery dates well in advance of the anticipated time of arrival of the items.

In general, all equipment shall be stored according to the manufacturer's requirements. If equipment and/or machinery is to be stored on site the Contractor shall either:

- Adequately package all items to enable the equipment and materials to be stored in the open without any deterioration whatsoever, or

- Provide an approved store, complying with the following minimum requirements:

  - Rotating mechanical equipment: Covered, ventilated, dust and vermin proof area.

  - Pipes, valves, steelwork etc.: Sheeted on open hard standing area.

The storage site as defined above shall be arranged by the Contractor at his own expense within the contract price.

The Contractor shall be responsible for the operation, safe keeping and maintenance of all equipment on site during storage and after erection up to the issue of the Operational Acceptance Certificate by the Employer.

Operation and maintenance of the equipment after the commissioning period and during the Contractor’s Defects Liability Period shall be the responsibility of the Contractor.

### Erection

The Contractor shall make his own arrangements for unloading of equipment and materials supplied and shall be responsible for any damage occurred. The Contractor shall at his own expense provide all tools, meters, gauges, temporary provisions as well as skilled and unskilled labour for the erection of the mechanical installations so that it shall be installed complete and in good working order.

If required by the Project Manager, for the proper installation of all mechanical equipment under this Contract an authorised representative of the manufacturer and its service organisation shall approve the installation and sign together with the contractor a statement with such approval. A form of such statement shall be provided by the Project Manager.

### Standards

For standards in general, see the Employer's Requirements, Document No 1: Design Basis. Standards for particular equipment are included where applicable in the following.

### Equipment and manufacture

The Contractor shall guarantee all mechanical equipment against faulty or inadequate design, improper assembly or erection, defective materials or workmanship, as well as leakage, breakage or other failure. Materials used shall be suitable for operation conditions.

All equipment shall be designed, manufactured and assembled in accordance with recognized and acceptable engineering and shop practice and selected for long life and minimum maintenance. Individual parts shall be manufactured to standard sizes to the extent possible, so that repair parts furnished at any time shall be installed on site.

Mechanical equipment shall be new and shall not have been in operation at any time prior to delivery, except as required by tests.

Mechanical equipment manufacturers to be proposed as vendors shall have ISO 9000:2000 quality system certificate.

It is the Contractor's responsibility to ensure that the components of the systems shall be compatible as to dimensions, ratings and operational characteristics and integrated to form a fully efficient system complying with the specifications.

All equipment and materials, which shall be provided to be used in pertinent works, shall be submitted to the Project Manager's approval together with operating capacity, certified test reports and other necessary information. Project Manager shall not accept any equipment or material which is not as per specification.

Warranty period of all offered mechanical equipment shall be two (2) years after the Operational Acceptance of the plant by the Employer, following installation and proper operation. The Contractor shall be responsible for draw-up of warranty certificates of these equipment in the name of The Employer and/or End Recipient and hand over the original copies to the Employer and/or End Recipient. Any defects or failure within warranty scope and period shall be fixed up in the liability of the Contractor. In such cases; the Contractor shall be involved in not later than 10 days after written communication from the Employer and/or End Recipient considering the urgency of the case. The Contractor shall be responsible for fix-up of damages in the equipment and paying costs due to the lateness in and evasion of his obligations stipulated in the Contract.

### Machinery guards and labelling

Machinery shall be guarded to prevent injury to persons, and meet international and local safety regulations.

Adequate guards shall be supplied and installed throughout the installation to cover all drive mechanisms. All rotating and reciprocating parts, drive belts etc. shall be securely covered to the satisfaction of the Project Manager to ensure the complete safety for both maintenance and operating personnel. However, whilst all such guards shall be of adequate and substantial construction, they shall also be readily removable for gaining access to the equipment.

The Contractor shall arrange for the supply and fitting of warning labels for all machinery operated under automatic control.

All identification information and warning labels shall be in English and Turkish language.

Guards for machinery shall be constructed of stainless-steel mesh or other corrosion resistant material. Means of set bolts or studs in tapped holes shall attach guards for parts that need to be examined. Self-tapping screws shall not be used.

All machinery guards and safety-related installations shall fully comply not only with relevant international standards but also with the provisions of the Machinery Safety Regulation (2006/42/EC as transposed into national legislation). The Contractor shall ensure that all safety measures, guards, and labelling are in accordance with this regulation throughout the design, supply, and installation phases.

### Lubrication

Lubrication systems shall be designed to operate with minimal maintenance requirements and shall not require servicing more frequently than once per week under continuous operating conditions. Such systems shall function without requiring intervention during start-up or shutdown, and shall be designed to minimize lubricant waste.

Lubrication points shall be easily accessible and conveniently located. Oil fill ports and drainage outlets shall be reachable from standard operational platforms or designated access areas. Drains shall be positioned to allow waste oil to be collected in appropriate containers without the need to disassemble or reposition the equipment.

The Contractor shall supply lubricants recommended by the equipment manufacturer in quantities sufficient to fill all lubricant reservoirs. The quantity shall also cover expected consumption during testing, site acceptance, and initial operation, up to the point of final delivery and formal acceptance of the equipment by the Employer.

Furthermore, a list of recommended lubricants and their equivalents shall be included in the operation and maintenance instructions. The lubricants recommended shall be available in Türkiye. The quantities shall be based on operating hours of 24 hours per day.

A list of recommended lubricants and their equivalents shall be included in the operation and maintenance instructions.

## Corrosion Protection

### General

Mechanical equipment shall be protected against corrosion by painting or other convenient treatment to a degree sufficient for the intended function and placement of the actual works.

All bright metal parts shall furthermore be covered before shipment with an approved protective compound and adequately protected during shipment to site. After erection these parts shall be cleaned.

Where the Contractor has a possibility to select different coatings that comply with technical requirements then the coating that has the smallest possible impact on workers health and safety shall be used. Documentation of the choice shall be made available to the Project Manager.

Dry surfaces, e.g. outer sides of valves, shall be categorised to C3 in ISO 12944 and shall be protected against corrosion accordingly. Wetted or submerged surfaces, e.g. inner sides of valves, shall be categorised to IM2 in ISO 12944 and shall be protected against corrosion accordingly.

### Galvanizing

Where steel or wrought iron is to be hot-dip galvanized, it shall be carried out by the hot-dip process and shall conform in all respects with EN ISO 1461.

Attention shall be paid to the detail of members in accordance with EN ISO 14713. Adequate provisions for filling, venting and drainage shall be made for assemblies manufactured from hollow sections. Vent holes shall be suitably plugged after galvanizing.

All surface defects in the steel including cracks, surface laminations, laps and folds shall be removed in accordance with EN 10113. All drilling, cutting, welding, forming, unit members and assemblies shall be completed before the items are galvanized. The surface of the steel to be galvanized shall be free from welding slag, paint, oil, grease and similar contaminants.

The additional weight of the items after being galvanized shall be not less than 700 grams per square meter of galvanized surface in line with TS EN 1561 Any kind of galvanized items to be used for the Works shall be met at least this requirement and the Contractor shall submit the relevant certificate to the Project Manager for approval.

During off-loading and erection utmost care shall be taken in order to avoid any damages to the galvanized surfaces. Galvanized items in stock shall be stacked so as to provide adequate ventilation to avoid wet storage staining.

Small areas of damaged galvanized coating shall according to agreement with the Project Manager in every case, be restored by:

Cleaning of the area of any weld slag and thoroughly brushing to provide a clean surface

Application of two coats of zinc-rich paint or application of a low melting point zinc alloy repair rod or powder to the damaged area, which is heated at 300C.

Where galvanized steel shall be in contact with aggressive solutions and/or atmospheres, the galvanized surfaces shall receive further protection by painting in accordance with the paint specifications given below.

The geometry of galvanized steel parts shall be thoroughly checked after galvanising. Any deformations shall be corrected without damaging the zinc layer.

Inspection and Documentation of Hot Dip Galvanising

The inspection and quality assurance of the hot dip galvanising carried out by the Contractor shall be in conformity with EN ISO 1461. Documentation for this inspection and quality assurance shall be issued and become part of the Quality Assurance documentation. After components have become hot dip galvanised, machining is not allowed.

### Painting in particular locations

The painting specifications shall be applicable to metal surfaces in the below mentioned locations:

A. Indoor location

The surfaces shall be not liable to liquid splashing or aggressive atmospheres.

B. Outdoor location

The surfaces shall be liable to rain and/or splashing from non-aggressive liquids. The surfaces shall not be liable to aggressive atmospheres.

C. Immersed location

The surfaces are below liquid level in aggressive or non-aggressive solutions, or the surfaces shall be liable to aggressive atmospheres.

The color schemes for the applied final paints shall be presented for and approved by the Project Manager.

All preparation and painting at works shall be carried out under cover at ambient temperatures controlled between 16 and 21°C and as agreed with the Project Manager. Painting shall not be carried out on surfaces which are not absolutely dry.

### Preparation and painting of steel work

Preparation and Initial Protection of Steelwork in Locations A and B

Works preparation shall be carried out when all machining has been completed and all traces of grease removed. In the case of welded steel works all slag and splatter shall be removed from the area of welds by chipping prior to sandblasting and priming.

All steel other than stainless steel shall be sandblast to grade SA 2½ and given a priming coat of an approved polyamide cured Zinc Phosphate Epoxy - double layer to provide a dry film thickness of at least 50 microns above peaks. The prime coating shall be applied with an airless spray process within 4 hours after sandblasting.

Galvanized steel shall remain unpainted in these locations.

Preparation and Initial Protection of Steelwork in Location C

Works preparation shall be carried out when all machining has been completed and all traces of grease and welding slag and splatter removed.

All steel other than stainless steel shall be prepared and hot-dip galvanized to EN ISO 1461.

Initial protection of hot dip galvanized surfaces shall comprise:

Thoroughly cleaning and de-greasing of all surfaces followed by etching with T-wash according to EN ISO 12944 and EN ISO 14703.

Washing with clean water, completely dried and given a priming coat of an approved Polyamide Cured Zinc Phosphate Epoxy - double layer to a dry film thickness of not less than 40 microns.

First Finishing Paint in Locations A, B and C

To surfaces in location A one coat of an approved Polyamide Cured Epoxy Micaceous Iron Oxide double layer shall be applied by brush or airless spray to give a dry film thickness not less than 125 microns. First finishing paint shall be given within 48 hours after application of priming coat.

To surfaces in location B and galvanized surfaces in location C one coat of an approved Polyamide Cured Epoxy Coal Tar double layer shall be applied by brush to give a dry film thickness not less than 125 microns. First finishing paint shall be given within 48 hours of priming coat.

Final Finishing Paint in Locations A, B and C

Surfaces in location A shall be given sufficient coats of approved Silicone Alkyd Enamel to give a dry film thickness of not less than 50 microns.

Surfaces in location B and C shall be given one coat of an approved Polyamide Cured Epoxy Coal Tar to give a dry film thickness of not less than 125 microns.

The total paint thickness on final inspection of the works shall not be less than:

Surfaces in location A - 200 microns

Surfaces in location B and C - 300 microns.

The colour of the final coating shall be approved by the Project Manager.

Cast Iron

Cast Iron and Ductile Iron shall be protected with first and final finishing paint as described above according to the actual location. The total paint thickness shall conform to the requirements stated.

Electric Motors and Enclosures

The surfaces of motors, gear enclosures shall be to the manufacturer's recommended finish according to location and shall be given sufficient coats at site of approved Silicone Alkyd Enamel to give a dry film thickness of not less than 50 microns.

Inspection of Corrosion Protection

Prior to the termination of the defect liability period a visual examination of the surface treated constructions and components shall be carried out. If rust or blisters is visible and these failures shall not be assigned to normal wear nor impact damages, the Contractor shall without any expense to the Employer mend the damages in conformity with a repair procedure approved by the Project Manager.

## Steel Constructions

Steel constructions shall be designed as to resist the static and dynamic forces they are exposed to. The Contractor shall specify in his offer the most important materials used.

Where risk of galvanic corrosion persists, galvanic separation shall be required.

### Structural steel

Structural steel shall be selected from EN 10025: part 2: 2004 of an appropriate grade and be accompanied by a materials certificate in accordance with EN 10204-3.1B.

Where risk of galvanic corrosion persists, galvanic separation shall be required.

### Wrought steel

Where not otherwise specified, wrought steel parts shall be selected from appropriate grade of EN 10083 and be free from blemishes, shot or hammer marks.

The steel shall be suitable for hot dip galvanizing. Serious rust shall not be found.

The Contractor shall submit for the approval of the Project Manager, the grade number selected for the various components.

### Cast iron

All grey iron castings supplied shall be to the appropriate grade in EN 1561. All castings shall be free from blowholes, flaws and cracks.

No plugging, filling, welding or "burning-on" shall be accepted.

### Stainless steel

Stainless steel used throughout the wastewater treatment plant shall be provided in accordance with EN 10088-1 grade 1.4404 (AISI 316L) or be of better quality, if not specified otherwise. All other parts in the plant specified as stainless steel shall be min quality 1.4307 (AISI 304L). However, the Contractor shall determine if the stated minimum requirements shall be sufficient for the particular application and if necessary, select a higher grade.

Material thickness in constructions of stainless steel shall be at least 3 mm when not otherwise stated. Welded tubes shall have a wall thickness of at least 2 mm.

Material certificates shall be required for all stainless steel to be incorporated in the works. Certificates shall comply with EN 10204-3.1B. Certificates shall be part of the QA-documentation

All stainless-steel material, pipes, flanges etc., shall be stamped according to their type, grade and pressure class. In addition, all stainless steel shall be accompanied by an authentic manufacturer's certificate to enable verification of origin and date of manufacture.

### Aluminium and aluminium alloys

Due to the corrosive atmosphere, the use of aluminium or aluminium alloy requires the approval of the Project Manager in all cases.

Immersed installations or installations which are periodically immersed shall not be constructed from aluminium or aluminium alloys.

If used alloys shall be of a type used for marine applications with magnesium as the main additive.

## Welding

### Welding in general

All welders shall be qualified and have a valid certificate according to EN 287-1 from a recognized testing institute. The certificate shall prove that the welder has passed the tests satisfactorily.

All welds in pipe joints shall be carried out in accordance with Welding Procedure Specifications (WPS) issued for each particular type of weld and material according to EN 288. The Welding Procedure Specifications shall be filled in or approved by an independent body, approved by the Project Manager, before welding.

All welding works shall be performed under the most convenient working conditions; hence all welding work shall be carried out at the manufacturer's workshop. Field welding shall be allowed only after prior approval by the Project Manager. Modern, effective equipment and techniques and latest welding technologies are to be utilised. All welding shall be performed by welders qualified and experienced in the particular type of welding required. It shall be the responsibility of the Contractor to ensure that all welding operators shall be properly qualified and competent to carry out all required field welding.

Records of welding procedures and welder performance qualification tests for work done shall be maintained by the Contractor for review by the Project Manager.

The method and procedure adopted for welding in workshops and at site shall be approved by the Project Manager before production starts.

#### Welding Procedure Qualification

The Contractor shall submit detailed welding procedure specifications complying with EN 287-1. All dimensions, all combinations of materials to be joined and all repair welding shall be covered by the procedure specifications. The procedure specifications shall be subject to the approval by the Project Manager.

The Project Manager shall at sole discretion approve the use of already established, sufficiently tested and documented procedures not more than two years old. Transfer of welding procedure qualification records from one contractor to another shall not be permitted.

For each procedure specification and prior to start of production welding the Contractor shall carry out welding of test joints under site conditions following all of the details of the approved procedure specifications.

The qualification test shall be carried out on steel with the highest specified minimum yield strength/maximum carbon equivalent which is expected to be covered by the Welding Procedure Specification. All the results from the procedure qualification records shall be submitted to the Project Manager for approval of welding procedures.

#### Qualification of Welders and Welding Operations

Only skilled welders and welding operators who shall document qualifications relevant for pipeline welding shall be accepted by the Project Manager. Prior to the performance of any production welding operators shall qualify for the relevant welding procedures according to EN 287-1.

The qualification tests shall be acceptable if they meet the requirements for visual examination, destructive testing and for radiographic examination as specified in EN 287-1. The testing shall be carried out by an approved laboratory at the Contractor's expense. Welder and welding operator performance test certificates shall be issued and kept on site during the whole working period.

Welder and welding operator qualification tests shall be performed together with welding procedure qualification tests. These certificates shall be only valid for six months after the last welding.

#### Welding of Pipelines

The Contractor shall supervise the site, the welders and their work during the entire working period. For this purpose, the Contractor shall use a qualified welding engineer or alternatively, if accepted by the Project Manager, an engineer with documented thorough theoretical knowledge and practical experience in the performance and evaluation of the welding work.

The welding shall be inspected by an independent inspection company engaged by the Contractor. It shall be the sole responsibility of the Contractor to document that welding and welding inspection fulfils all specified requirements.

#### Welding Preparation

Items material grades, wall thicknesses and pressure ratings shall conform to the requirements laid down in the applicable drawings and specifications.

Each pipe or component shall be visually inspected to ensure that it has not sustained any visually determinable damage. Disposition of damaged items shall be resolved in consultation with the Project Manager.

All requirements for welding preparation contained in the qualified welding procedure specification shall be strictly adhered to.

#### Welding

All welding shall be performed by qualified welders and strictly in accordance with qualified welding procedures.

Welding shall be suspended by the Contractor when prevailing weather conditions shall impair the quality of the work, e.g. airborne moisture, blowing sand, high winds or thunderstorms.

Stray arching outside the weld groove shall be not permitted. shall stray arching outside this area occur, this shall be brought to the attention of the Project Manager who shall require any such damaged section to be repaired or cut out at the Contractor's expense.

Each pass shall be completed around the whole circumference before the next pass is started.

The position of start/stop on subsequent passes shall not be identical.

No welded joints shall have less strength than the joined parts.

Upon completion of the weld and the pipe surface shall be cleaned of weld spatter and other deposits, and shall then be wrapped with a dry waterproof insulating mat to ensure a slow cooling of the weld zone and to give protection against rain.

#### Materials

The weld filler metal selected shall give a weld metal matching the base metal properties as closely as possible. The yield strength of consumables shall neither overmatch the base material yield strength by more than one level in EN 499, nor shall under matching be allowed.

#### Cleaning of Carbon Steel Items after Welding

The surface shall be dry and free of oil, grease, soil and concrete residues. All loose rust and mill scale shall be removed by wire brushing immediately before welding inspection. On straight pipes brushing shall be done mechanically using sharp brushes to avoid polishing of the steel surface. Therefore, a stock of readily accessible new brushes shall be required.

Welds fabricated with basic filler metals shall be washed with fresh water.

Cleaning by sandblasting to grade Sa2 shall be allowed as an alternative.

#### Identification of Weld Seams

Every girth weld shall be numbered by the Contractor in accordance with a system to be specified by the Project Manager. This number shall be painted on the pipe coating on one side of the joint between 0.5 m and 1.0 m from the seam together with the pipe number and pipe length to facilitate completion of the pipe book.

For each pipeline and each pressure test section, the Contractor shall fill in pre-printed forms and enter these in a pipe log. As the work progresses, the Contractor shall present the pipe log forms to the Project Manager. Before the start of a pressure test, the completed pipe log for the section in question shall be handed over to the Project Manager.

#### General Requirements, Welding Inspection

Examination shall be performed according to this specification and the following codes and standards:

Radiographic examination according to ISO 1106, Part 3, Recommended Practice for Radiographic Examination of Fusion Welded Joints. Fusion Welded Circumferential Joints in Steel Pipes of up to 50 mm Wall Thickness.

Ultrasonic examination according to ASME Boiler and Pressure Vessel Code, Section V, Non-destructive Examination, Article 5, Ultrasonic Examination Methods for Materials and Fabrication.

Magnetic particle examination according to ASME Boiler and Pressure Vessel Code, Section V, Non-destructive Examination, Article 7, Magnetic Particle Examination.

Liquid penetrate examination according to ISO 3452, Non-destructive Testing, Penetrate Inspection, General Principles.

Visual examination according to ASME Boiler and Pressure Vessel Code, Section V, Non-destructive Examination, Article 9, Visual Examination.

Hardness measurement according to ASTM E 110, Standard Test Method for Indentation Hardness of Metallic Materials by Portable Hardness Testers.

The Contractor shall engage a qualified independent inspection company which shall perform, evaluate and document all welding inspection. The inspection company shall be approved by the Project Manager.

All non-destructive examination shall be performed according to a written procedure. The procedure shall conform to the requirement of the adequate method standard and this specification. Procedures shall be submitted to the Project Manager for approval and shall be qualified to the satisfaction of the Project Manager.

#### Extent of Examination, Welding Inspection

All welds shall be 100% visually examined.

Thirty percent of the welds shall be tested. The following methods shall be applied as approved by the Project Manager:

Radio-graphic

Ultra-sonic

Penetration

The Radio-graphic method shall be used. However, if this method shall not be applied one of the other methods shall be used, as approved by the Project Manager.

Ultrasonic examination shall substitute radiography where radiographic examination is impractical and shall be used as general back-up for radiography in case of interpretation/verification problems.

Guarantee welds (welds which shall not be pressure tested) and tie-in welds shall be 100% examined by radiography as well as by ultra-sound.

Welds to be tested shall mainly be selected from those of which the backside of the weld shall not be visually inspected. Such welds shall be tested by the Radiographic or the Ultrasonic method. Selection of welds shall be carried out by an accredited independent agency, approved by the Project Manager.

All welds which have been repaired or replaced shall be 100% re-examined by the same methods and with the same acceptance criteria as required for the original work.

Socket welds and branch connection welds which are not radio graphed shall be examined by magnetic particle or penetrate methods to the extent stated for butt welds.

Where spot examination is required in subsequent sections, the welds shall be selected to ensure that the work of each welder and each welding procedure is included.

When required spot examination reveals defects, two additional welds, the preceding and the subsequent welds made by the same welder, shall be examined.

If one of these welds shows defects, three preceding and three subsequent welds shall be examined at the Contractor's expense.

If five or more subsequent welds of one welder show defects, all welds of this particular welder shall be additionally examined at the Contractor's expense.

10% of all butt welds shall be examined by radiography along their entire circumference as described above. The Project Manager shall specify greater extent of examination.

#### Acceptance Criteria

The accept criterion shall be class C in accordance with ISO 5817. The test shall be carried out by an accredited independent agency, approved by the Project Manager. A report on the tests shall be provided.

#### Production Testing

The Project Manager shall be entitled to select a number of seams for destructive testing.

The Contractor shall be responsible for cutting out the seams, bevelling the pipe ends and re-welding the joint. The destructive tests shall, unless otherwise agreed, be made in accordance with the requirements in the respective general welding specification covering qualification tests for welding procedures.

The Employer shall bear the cost of these tests, if the welds are proved to be acceptable. However, if it turns out that the seam does not comply with all the requirements, the Contractor himself shall bear the costs. In this case, the Project Manager shall insist on an additional seam being tested, and the costs of the testing and renewal of this seam shall be paid by the Contractor, irrespective of the results. If this seam does not comply with the requirements, the control shall be further extended at the Contractor's expense.

The extent of any such supplementary inspection work shall be decided by the Project Manager with the aim of establishing in a satisfactory manner whether the welding work complies with the requirements or not.

If any change of personnel takes place during the course of the welding work, this could influence the quality of weld seams and the Project Manager shall require a new seam to be destructively tested at the Contractor's expense.

#### Document Requirements

The following documents shall be required before examination:

Certificates for NDE personnel

NDE procedures

Report forms

Request for deviations, if any, from specified requirements

During examination:

Field reports

After examination:

Authorised examination reports with enclosed field reports and films.

#### Coating of Weld Seams

Upon successful completion of all inspection procedures, the weld seams on carbon steel items and their surroundings shall be carefully cleaned and protected with an internal and external coating as specified in item 7.2.

### Welding of carbon steel

Acceptable welding processes shall be:

Shielded Metal Arc Welding (Stick) SMAW

Gas Tungsten Arc Welding (TIG) GTAW

Gas Metal Arc Welding (MIG/MAG) GMAW

Flux Cored Arc Welding FCAW

The use of welding processes other than those listed above shall be permitted only with the prior approval of the Project Manager. Processes shall be used in combination if the same combination and sequence of processes have been qualified by the welding procedure qualification test.

Prefabrication in workshops shall be used to the maximum extent possible.

For the welding of carbon steel pipes, the AISI code B 31.1 and API Std. 5L recommended practices shall apply. Welded structures shall comply with EN 729-3

### Welding of stainless steel

For welding of stainless-steel pipe, the AWS D10.4-79 shall apply.

The welding method shall be the tungsten inert gas method (TIG) or the metal inert gas method (MIG) for workshop as well as on-site welding. Irrespective of the method chosen the inner surface of the weld shall be protected by clean inert gas. When welding the oxygen content of the mixture oxygen/inert gas shall not exceed 20 ppm.

In order to guarantee high quality welded joints, piping and other quality stainless steel components shall as far as possible be prefabricated in workshop.

For stainless steel welding the following shall be observed:

Only butt weld jointing of pipes shall be allowed during erection work,

Where butt welds shall be used, the penetration shall be completed, if necessary, with root run,

Backing rings shall not be used,

No surface defects reducing the corrosion resistance or discoloration of the surface shall be accepted,

After welding the weld shall be carefully pickled and passivated, and

The welds shall be thoroughly washed in clean water after pickling and passivation.

## Bolts

Steel-bolts shall be provided according to ISO 8.8 according to EN 20898-1 and EN 20898-2. Stainless steel bolts shall be provided according to ISO 3506-1 and 3506-2 in grade A4, Class 70 or 80.

Bolts shall have an over-length of minimum 3 mm and maximum 12 mm for bored in or embedded bolts as well as flanged joints.

All necessary bolts, nuts, washers and anchor plates shall be supplied together with the joints. The bolts and nuts shall be high tensile steel with metric treads, and with hexagon heads.

All bolts, screws, nuts and mounts shall correspond to the material secured by bolts. This also applies to chemical anchors.

Bolts, washers and nuts for galvanised steel items and for coated steel items shall be hot dip galvanised. Washers shall always be used for bolts fastening coated steel in order to prevent destroying the coating.

Bolts, washers and nuts for stainless steel items like flanges shall be of stainless steel of similar grade or higher.

To prevent galling, strain hardening, crack and contact corrosion, it shall be necessary to apply molybdenum-sulphide or similar to thread and washers.

### Chemical anchors and anchor bolts

Holding down bolts of sufficient length shall be provided and fixed for securing the whole of the machinery to the foundation.

Chemical anchors shall be supplied in quality suitable for conditions under which they shall be permanently exposed to the action of water.

Alternatively, an injection technique shall be applied.

Fixation of mechanical equipment to concrete structures shall be done by anchor bolts, which shall be placed during casting, or by drilling. No anchor bolts shall get in contact with reinforcement bars in the concrete structure. Anchor bolts used for installation of stainless-steel equipment shall be made of stainless steel of equivalent quality.

For all other purposes hot dip galvanised anchors shall be applied.

## Steel Pipework

All pipes and assembling parts under this Contract shall be of first quality, truly circular, and uniform thickness, free from scale, lamination and other defects, and shall be designed and suitable for the operational pressures and temperatures.

Pipeworks shall be arranged, as to ease the dismantling and removal of pumps or major items of equipment i.e. by the installation of dismantling joints where appropriate.

Expansion and dismantling joints shall be double flanged. Dismantling joints shall be able to withstand the total tension loads from the maximum pressure occurring in the pipes.

A dismantling joint shall be included in the suction and delivery pipework of all pumps for easy dismantling.

All pipework shall be fixed adequately with supports. When passing through walls, pipework shall include puddle flange.

In addition, all stainless steel shall be accompanied by an authentic manufacturer’s certificate to enable verification of grade, origin and date of manufacture. All pipes shall comply with EN 10217-7 accompanied with a test certificate according to EN 10204 / 3.1B. The certificates shall be part of the QA-documentation.

All piping inside buildings up to 1m outside the buildings shall be made of stainless steel, see item 7.3.4. Other materials shall only be accepted after prior acceptance from the Project Manager.

All piping inside shall have permanent marking, stating standards and material identification numbers.

Pipe ends shall be sealed with PVC cabs during transportation.

Welded stainless steel pipes shall have a wall thickness of at least:

| Internal diameter (mm) | Wall thickness (mm) |
| --- | --- |
| 200 or less | 2.0 |
| 250 | 2.5 |
| 300 | 3.0 |
| 400 | 3.0 |
| 500 | 4.0 |
| 600 | 4.0 |

### Pipes from stainless steel

Pipe work for aquatic, biogas and air media shall be stainless steel 1.4404 (AISI 316L) pipes if not otherwise stated. Material shall be according to requirements for stainless steel specified in item 7.3.4.

Pipes shall be according to EN 10217-7. Pumping mains and pressure pipes shall minimum be rated for PN 10.

### Pressure test of pipes

The Contractor shall perform pressure tests according to the following instructions for all pressure piping.

The Contractor shall advise the Project Manager in due and shall provide and mount all for the pressure tests necessary equipment.

If pressure tests shall be made against closed valves the guidelines from the manufacturer of the valves regarding the highest single side pressure against closed valve shall be complied with.

Hydraulic pressure tests shall be carried out by the use of potable water.

During pressure tests a minimum of 1.5 times maximum allowed operating pressure shall be maintained. Water shall be forced into the pipes by means of a force pump fitted with a pressure gauge to indicate the pressure at the lowest point in the section under test. Pipelines shall not be accepted until they have withstood the required pressure for 30 minutes without leaking and without the pressure dropping.

Pressure tests shall be according to API 5L, TS 10217 and DIN 1626.

The Contractor shall prior to pressure testing verify on the spot that the piping is fully evacuated from air.

After successful and approved pressure test the piping shall be emptied and the pressure test fluid shall be disposed of.

If it is not possible to perform visual inspection of leaks of all welded joints, the piping shall be tested according to the following guidelines:

Piping shall be tested with a test pressure of minimum 1.5 times maximum allowed operating pressure. The pressure shall be held for at least four hours.

During the pressure hold period no water shall be allowed to be added, and

All visible welding joints, flange joints and glands on valves and pumps shall be inspected.
The acceptance criterion demands no detected leaks.

After the pressure tests have been finalised, the Contractor shall elaborate a report, a copy of which shall be submitted to the Project Manager. The report shall as a minimum include:

Pressure Test Procedure,

Unambiguous references to piping or part of piping and shut-off,

Specification of test pressure,

The period of the pressure tests,

Results and signature of acceptance, and

A description of atypical testing results, their causes and corrective action.

### Flanges

Flanges for stainless steel pipes shall be executed as loose flanges of similar quality as the piping.

All flanges shall be rated for PN 10 and drilled according to DIN 2501. In the case the operating pressure requires PN25 components welded neck flanges according to DIN 2634 shall be installed.

### Pipe bends

Bends shall have minimum the same wall thickness and be of same material grade as the joining pipes. Execution according to DIN 2605. Radius 1.5 x D.

### Tapers

The tapers shall be made of stainless steel see item 7.3.4. In general, all tapers shall be of the concentric type, similar to DIN 2616.

Suction intake tapers for pumps, however, shall be of the eccentric type. The installation of the taper for dry installed pumps shall be with the straight side at the top. The length of the taper shall not be less than 0.5*(D+d).

### Flush appliances

The flush appliances shall be made out of stainless steel see item 7.3.4.

Each section, which shall be separated from the overall piping system, by valves, shall have a sufficient number of connections for drainage and cleaning. The exact number and location of connections shall be decided jointly with the Project Manager.

A flush connection comprises:

- pipe socket DN 50 with outer thread 2“, approx. 100 mm long

- socket globe valve DN 50

- C-coupling with outer thread 2” according to DIN 14 307, material: brass

- C-blind coupling according to DIN 14 311 complete with chain, material: brass.

### Branch pipes

Wherever possible, sockets according to DIN 2618 shall be used. Tees DN 65 and smaller shall be according to EN 2615

### Measuring instruments

Wherever from a process engineering or operational point of view the necessity to install measuring instruments arises, the required socket or flange connections shall be provided on the pipelines.

### Vent pipes

The vent pipes shall be made of stainless steel 1.4404 (AISI 316L) see item 7.3.4. Depending on the pipe arrangements, vent pipes including valves shall become necessary. Generally, vent pipes shall terminate in “safe“areas, e.g. above roofs. The arrangement of the pipes shall guarantee unobstructed ventilation.

### Pipe brackets

All pipe brackets shall be of stainless steel 1.4404 (AISI 316L) in accordance with item 7.3.4. Pipe bracket arrangements shall consist of sliding and fixed brackets. Design and installation of sliding brackets shall guarantee proper alignment of the pipe, even when the pipe is moving longitudinally. No stress shall be transmitted to the supports, except for the weight resulting from pipe and medium. The design of the fixed brackets shall be such that all forces and moments resulting from operating conditions shall be safely transmitted onto the building structure. Required pipe supports, gussets, etc. shall be connected to the pipes by reinforced welds.

The design of the brackets with respect to axial movement, static and dynamic forces e.g. from water hammer etc. shall be based on the prevailing operating and ambient temperatures of the pipe system in question.

All brackets and pipe components being inaccessible after installation shall be sufficiently protected against corrosion prior to assembly.

### Installation of piping

Pipelines shall be level, plumb and properly aligned, respectively installed to the required slope. Utmost attention shall be given to all pipes connected to machinery and appliances for not transmitting forces and moments to the equipment. Forces and moments due to misalignment of pipe work shall under no circumstances be transmitted to duct walls.

## Stairs, Walkways, Platforms and Handrails

All stairs, walkways, platforms and handrails shall be made compliant to the current local requirements (i.e. occupational health and safety regulation under 6331 numbered laws.).

All open sides of stairs, landings, walkways and platforms shall be guarded with handrails. Handrails shall include top handrail, intermediate rail, handrail, balusters and toe kick plates. Two hanging chains shall guard access openings to stairs and ladders, which shall be secured at one end and detachable at the other.

The height of the handrails shall be 1,100 mm with an intermediate rail at a height of 550 mm. Handrail height shall be measured vertically from finish floor level to the handrail centreline. The height of toe plates shall be 150 mm. Toe plates shall be fixed securely to the stanchions and/or balusters.

Sloping handrails shall be as specified for horizontal handrails, but with top rail 900 mm vertically above the line of pitch and stanchions vertical and spaced at not more than 1,500 mm measured parallel to the line of pitch.

All mounting flanges shall be of substantial construction, with horizontal flanges drilled for not less than three bolts with two bolts on a line parallel to and on the walkway side of the line of handrails. Vertical flanges shall be drilled for not less than two bolts, the lines through the bolts being vertical. Fittings shall be screwed or secured by means of grub screws. Bolts, nuts, washers to be used for fixing shall be with galvanised.

Handrails shall be able to withstand a vertical force of minimum 0.8 kN/m on the top rail. The deflection of the rails shall not exceed 0.8% of the span between stanchions, and the deflection of stanchions shall not exceed 0.8% of their height.

Handrail and balusters shall be manufactured from either aluminium, hot dip galvanised steel or stainless-steel tube with bore not less than 32 mm (1 ¼ in). Toe plates shall be of 5 mm thick aluminium, hot dip galvanised steel or stainless-steel plate. Distance between balusters shall not exceed 1,500 mm.

Handrails, balusters and toe plates shall joint with euroclamp connector to facilitate easy installation and to provide a smooth and neat appearance. Welding joints shall not be accepted. The Contractor shall ensure that unless specified to the contrary all handrails shall be prefabricated and of uniform appearance and manufacture.

The Contractor shall submit working drawings of the handrails to the Project Manager for approval.

### Staircases and galleries

Stairs shall have handrail on both sides. The height of the handrail on stairs shall not be less than 900 mm. If handrail shall be attached to a wall, it shall have at least 75 mm clearance from the wall.

Staircases shall preferable be within 38-45° with riser/go dimensions in accordance with the formula: Twice the riser plus the go shall not be less than 572 mm nor more than 635 mm. Overlap shall be minimum 16 mm.

Staircases shall be designed to carry a uniform load of 3.5 kN/m2 in addition to dead weight and loads during operation calculated on the plan area of the stair. The Contractor shall design the staircases for the actual point-load adequate for the equipment to be unloaded, however, no less than 3.0 kN in the middle.

Treads shall be with non-slip pattern surface.

Material: Hot dip galvanised steel in line with item 7.2.2.

### Access ladders

Ladders shall be fabricated of mild steel and hot dip galvanised after fabrication. The stringers shall be flat section not less than 65 mm x 13 mm spaced 380 mm apart and shall be flanged and drilled for wall fixing at both ends. The distance between stringers shall be widened over the top where they shall be not less than 600 mm apart. Ladders over 3,000 mm long shall have additional intermediate stays at not more than 2,500 mm centres.

Rungs shall be 25 mm diameter solids at 300 mm centres riveted or welded to the stringers. Rungs shall be not less than 225 mm from the wall.

All ladders shall have safety cages, which shall be constructed of three flat vertical strips supported by flat hoops, with a diameter of 750 mm. The hoops shall be approximately 700 mm centres and the first hoop shall be 2,400 mm above ground or platform level.

Where the rise exceeds 6,000 mm an intermediate landing shall be provided.

### Open mesh and chequer plate flooring

Open mesh flooring and gratings shall generally comply with EN ISO 14122 except where otherwise specified hereinafter. Such flooring and gratings shall be of rectangular mesh and non-slip and shall be mild steel and hot dip galvanised after manufacture. Alternatively open mesh and chequer plate flooring shall be of stainless steel 1.4307 (AISI 304L) or glass fibre reinforced polyester.

Flooring shall be adequately supported by means of substantial members.

Flooring shall be designed to carry a uniform load of 3.5 kN/m2 in addition to dead weight and operational loads. The Contractor shall design the flooring for the actual point-load adequate for the equipment to be unloaded, however, no less than 3.0 kN in the middle.

The deflection shall not exceed 0.2 percent of the span. Flooring shall be provided with curbing at the edge of walkway. Each floor panel shall be separately secured to the supporting members by means of fixing brackets. However, each floor panel shall be secured in a way that when not fixed by brackets it shall be fixed in all horizontal directions.

Both the load bearing and transverse bars in rectangular open mesh flooring panels shall be positioned symmetrically around the centre lines of the panels in both directions so that when the panels shall be fixed in extensive areas or in long runs, the bars of all panels shall be in line.

Chequer plate flooring shall be of the non-slip type, not less than 8 mm thick measured excluding the raised pattern. The flooring shall be secured to its frame by stainless steel countersunk screws.

All flooring shall be removable and set flush in frames of similar material. Where frames shall be fixed over openings the frames shall be provided with lugs for building in.

Flooring shall be provided in sizes suitable for lifting and removal by one man and with the appropriate cut-outs to permit its removal without disturbing or dismantling spindles, supporting brackets, cables or pipe-work.

### Hatches

Hatches shall consist of a frame with a hinged cover. The frame shall be designed for mounting in recesses in the concrete slab. Hatches on dry wells shall be watertight. Detailed design for sealing shall be subject to the approval of the Project Manager.

A handle for opening of the hinged cover shall be integrated in the cover. The cover shall be provided with a safety mechanism, which locks the cover in open position whenever opened. The mechanism shall be manually released before the hatch shall be closed again.

The hatches shall be designed to withstand a load of minimum 15 kN depending on the location.

Hatches shall be prefabricated and shall be from a recognised manufacturer specialised in the manufacturing of hatches for similar purposes.

Heavy hatches shall be provided with spring-loaded mechanisms or similar facilities which reduce the force required for safe opening and closing of the hatch.

The hatches shall be made of hot dip galvanised steel. Alternatively, hatches shall be made of stainless steel 1.4307 (AISI 304L).

## General Mechanical Equipment

Hoists, cranes and davits shall be provided everywhere necessary for the maintenance of the plant to avoid heavy lifts for the operation staff on the wastewater treatment plant, for example, equipment such as pumps, mixers, blowers, screens, dewatering equipment, etc.

The cranes, hoists and davits shall enable to bring the equipment to a point where further transport shall be possible e.g. by a fork lift.

### Lifting Equipment

#### Slewing davits

Slewing davits shall be provided for all pumps, mixers, etc. up to 150 kg, however a slewing davit shall be only required in case the pump and other equipment are not served by an overhead crane or electrical hoist.

The slewing davit shall be capable of lifting/lowering the submersible pump and/or mixers and shall have the following features:

- shall be permanent and installed with chemical anchor on floor.

- davit based on DIN 15018 H1 B2

- hoist in compliance with DIN 15020-1

- davit with manually operated wire hoist

- davit complete with all necessary fastening material (fastening material stainless steel according to 7.3.4)

- slewing radius of davit to be such to permit unloading of raised pump at a place accessible by forklift

- the lifting height shall be sufficient to allow slewing the crane with pump or mixer to pass the obstacle height (e.g. handrail)

- davit including all accessories shall be in accordance with current national safety regulations

Materials

- davit: hot dip galvanized steel, stainless steel structure or aluminium

- manual wire hoist: seawater resistant aluminium, or stainless steel, with safety ratchet block

- lifting wire, thimble and shackle: stainless steel

- pulley: polyamide

#### Jib Crane with electrical

Jib crane shall be electrically operated for service lifting equipment with a mass exceeding 150 kg.

Electrical jib crane shall be equipped with precision hoisting gear to allow accurate and sensitive lifting and lowering. Breaks to secure load in case of power failure.

Supply shall include all electric cabling necessary for operation. All connections shall be equipped with vibration proof terminals. All motors to be protected by means of thermistor protection. Limit switches for all final positions. Local switch cabinet for each crane equipped with pilot lamp, switches and an emergency cut-out for all actuators. Limit of delivery shall be terminal block in the switch cabinet. The body of electrical chain hoist shall be of aluminium die cast and minimum IP 55.

Plug-in connection or wireless push button control with emergency stop switch for remote control shall be provided. It shall contour to comfortably fit into hand. The button has a light operating sensation which responds to fine adjustments in pressure.

The jib crane shall be rated for the heaviest single lift under erection or maintenance operations.

Load (lifting) chains shall be stainless steel and/or hardened hot dip galvanized steel, and be able to reach the floor/ground.

The maximum load shall be clearly marked with large easy reading figures/letters on the crane.

The Jib crane shall have an adjustable mast and horizontal boom. Mast shall be fixed with chemical anchor on ground/ floor.

The Jib crane shall be able to slew 180 degrees pillar mounted and have adjustable rotation stop with 10° increments. It shall be 3-position lock (–90°, 0°, +90°).

The capacity rating of jib crane shall exceed maximum weight of materials to be handled. Each of crane capacity shall subject to the Project Manager’s approval.

Under boom height shall exceed the lifting distance required for effective materials handling. Each of crane under boom height shall subject to the Project Manager’s approval.

#### Electric Chain Hoist with Monorail

The hoist shall be rated for the heaviest single lift under erection or maintenance operations. Load (lifting) chains shall be stainless steel and/or hardened hot dip galvanized steel, and be able to reach the floor/ground.

The maximum load shall be clearly marked with large easy reading figures/letters on the hoist.

Plug-in connection or wireless push button control with emergency stop switch for remote control shall be provided. It shall contour to comfortably fit into hand. The button has a light operating sensation which responds to fine adjustments in pressure.

Construction and assembling shall be according to local laws and regulations or if not available according to EN respective ISO standards.

Electric chain hoists shall be equipped with precision hoisting gear to allow accurate and sensitive lifting and lowering. Breaks to secure load in case of power failure. Supply shall include all electric cabling necessary for operation. All connections shall be equipped with vibration proof terminals. All motors to be protected by means of thermistor protection. Limit switches for all final positions.

Local switch cabinet for each hoist equipped with pilot lamp, switches and an emergency cut-out for all actuators. Limit of delivery shall be terminal block in the switch cabinet. Power supply for movable bridges and lifting devices via trailing cable or trolley wire.

The body of electrical chain hoist shall be of aluminium die cast and minimum IP 55.

The electrical chain hoist shall have a chain container which is made of durable plastic or canvas.

The electrical chain hoist shall have a counter –hour meter to show the hoist’s total on time and number of lowering starts.

The electrical chain hoist shall have motorized trolley fitted with drop stop and wheel climb prevention lugs (derailment). Rail manufactured as I-profile, corrosion protected according general specification shall be used for trolley track. Gearboxes, wheels and motors to be maintenance free.

To ensure safety, the electric chain hoist shall be equipped with friction clutch and upper lower (limit) switch. In addition to this electro mechanic or electromagnetic disk brake shall be in hoist for safety operation.

To prevent the motor from burning out due to the excessive usage, a standard thermal protector shall be installed in the motor.

#### Overhead Travelling Cranes

Longitudinaly and transversaly moveable, one or two beams due to static requirements, incl. electric cable hoisting gear.

Rail manufactured as I-profile, corrosion protected according general specification. Two speed drive for crane and trolley. Crane runway consisting of one or two beams (due to static requirement), incl. all rails, mounting plates and fixing material, attachments for cabling etc. and stop blocks for limitation of movement.

Crane bridge shall be distortion free and wheels of crane travel shall operate synchronously to avoid twisting. Crane bridges constructed as maintenance free box beam. Gearboxes, wheels and motors to be maintenance free.

Lifting with brake device with precision hoisting. Electric equipment integrated in trolley.

Control: If not mentioned otherwise by movable suspension switch.

Plug-in connection or wireless push button control with emergency stop switch for remote control shall be provided. It shall contour to comfortably fit into hand. The button has a light operating sensation which responds to fine adjustments in pressure.

Construction and assembling shall be according to local laws and regulations or if not available according to EN respective ISO standards.

Overhead crane shall be equipped with precision hoisting gear to allow accurate and sensitive lifting and lowering. Breaks to secure load in case of power failure. Supply shall include all electric cabling necessary for operation. All connections shall be equipped with vibration proof terminals. All motors to be protected by means of thermistor protection. Limit switches for all final positions. Local switch cabinet for each crane equipped with pilot lamp, switches and an emergency cut-out for all actuators. Limit of delivery shall be terminal block in the switch cabinet. Power supply for movable bridges and lifting devices via trailing cable or trolley wire.

### Ventilation

Forced mechanical ventilation shall be provided everywhere either safety, heat and/or odour problems are expected. Ventilation rate shall comply with national standards for health and safety.

Dry pumping stations, pump sumps, buildings for screens, blowers, sludge dewatering, technical gallery (if any), chemical building for phosphorous removal (if any) etc. shall be provided with mechanical ventilation systems.

In order to avoid odour emissions to the surroundings the inlet structures shall be covered and mechanically ventilated. The exhausted air from these structures as well as from the sludge dewatering facilities shall be exhausted in free air or treated in a bio filter if stated so in order to remove any odorous compounds which could cause nuisance complaints.

Whenever forced ventilation is required the noise level shall be minimised and not exceed the levels described in the Employer's Requirements, Document No 1: Design Basis.

All intakes and exhausts shall be covered for all weathers.

### Drive units

Drive units for the equipment shall be designed for 24 hours continuous operation. The nominal rating of the gear shall be at least equal to the nominal kilowatt output of the attached motor. Each gear shall be a totally enclosed unit with oil or grease lubricated antifriction rolling bearings throughout.

All drives, couplings and other moving parts shall be efficiently covered on all sides with safety guards.

Long-life seals on the input and output shafts shall be fitted up to prevent the escape of lubricant and the ingress of dust, sand and moisture.

Lubrication of bearings etc. shall be by either splash or forced feed system.

The Contractor shall ensure that the lubricants used for initial filling and specified in the maintenance manual is adequate for prolonged operation in ambient temperatures of up to 55C. without overheating.

The gearboxes shall be marked with manufacturer's identification together with the rated shaft speeds, output power and maximum ambient temperature.

### Bearings

All bearings shall be generously rated and sized to secure satisfactory and stable running without vibration under all conditions of operation for a minimum life of 50,000 hours running, which shall be certified or otherwise documented.

All bearing shall be to ISO or AGME standard and SI metric unit dimensions where practicable.

The intervals between lubrication shall be maximized (not less than 2 weeks) and shall be defined for each individual item and included in the operation and maintenance manual.

### Motors

#### General

Motors shall comply with the following general standards and norms:

- IEC 60034-1, 60034-5, 60034-6 and 60034-8, 60034-9.

- Relevant EN standards.

Motors shall be designed for the temperatures and humidity occurring on Site and the installation in which they operate.

- The motors shall be designed and marked for operating conditions according to IEC 60034-1.

- Unless otherwise specified in subsections, Motors with rated nominal power larger than 15 kW shall be delivered for soft starter or frequency converter.

- Motors for pumps shall be squirrel-cage asynchronous motors unless otherwise stated.

#### Mechanical Requirements

The degree of protection provided by enclosure for motors shall be minimum IP 55 to IEC 60034-5.

Protection grade for outdoor motors shall be minimum IP 55 and equipped with a drainage hole in the lowest point

The degree of protection for submerged motors shall be minimum IP 68.

The motors shall be cooled in order that the permissible operation temperature is not exceeded.

Motors shall be balanced according to ISO 2373 vibration class N.

Noise level shall minimum fulfil IEC 60034-9.

All motor covers shall be delivered efficiently protected against corrosion according to specifications in item 7.2 "Corrosion Protection".

Motors shall be insulated to class F in accordance with the IEC 60085. The limit of temperature raise during operation shall not exceed that for class B insulation.

#### Electrical Specifications

Motor performance and data shall be in accordance with IEC 60034-1 and shall legible be marked with:

- manufacture,

- serial number,

- rated power,

- full load current,

- voltage,

- cos

- frequency,

- number of phases,

- start current,

- rpm.

Each motor shall be provided with thermo-protection.

Motors larger than 5.5 kW shall have star-delta windings soft starters.

Motors larger than 10 kW shall be provided with thermistors in the windings for each phase.

Smaller motors shall be provided with bi-metal thermo-switches in case thermistors shall not be provided.

Submerged gearboxes shall be provided with moisture sensor.

The motors shall be designed for the following parameters:

- Voltage fluctuations +/- 5%. The voltage variations shall not result in a temperature increase in excess of what is stated in IEC 60034-1,

- Frequency: 50 Hz. Frequency variations +/- 2.5 Hz.

Motors shall be equipped with connection boxes with separate terminals for each winding end, and connection for protective conductor. The terminals shall be designed for twice the nominal current, however, minimum 2.5 mm2.

Thermo-switches shall be connected to separate terminals inside the connection box.

Marking of connections and rotation direction shall be in accordance with IEC 60034-8.

All motors shall be equipped with suitable number and dimension of cable glands.

All submerged pumps (and other motors) that shall be taken out of operation and lifted to ground level by a hoist (or in an equal way) shall have power supply and signal cables connected by CEE sockets enabling electrical disconnecting without use of tools. The sockets (the male as well as the female part) shall be mounted in a location where flooding is impossible. The sockets shall be protected against rain and other weather conditions as described for outdoor instruments in general. If these demands shall not be met the degree of protection shall be IP 68 to IEC 60529.

### Balancing

Revolving parts shall be balanced both statically and dynamically, so that for any combination of speed and load up to the maximum, there shall be no vibration caused by out-of-balance forces.

### Suppression of noise

All plant offered shall be quiet in operation. The noise level within the buildings shall not be more than 80 dB(A) if not otherwise stated. The Contractor shall ensure that all sections of equipment are designed such that when installed the noise emitted is no more than stated in the specific requirements and as stated above. The equipment shall also comply with the requirements of the Employer's Requirements, Document No 2.

### Penstocks

Penstocks shall be of the following types:

- Stainless steel in accordance with EN 10088-1 grade 1.4404(AISI 316L), with rubber sealing faces.

- Each manually operated penstock shall be provided with a suitable handle of adequate size for the duty required and the gearing shall be supplied where necessary to ensure that the required operating force applied by hand to the handle shall not exceed 250 N. The height of the operating handle shall be approximately 1 meter above operating level unless otherwise stated.

- The handles shall have cast on them the direction of closing, which shall preferably be clockwise.

- Electrically operated penstocks shall be provided with an adequately rated electrical drive (item 7.8.18).

- Spindles shall have machine cut robust trapezoidal or square form threads. They shall be of stainless steel (item7.3.4), manganese steel or manganese bronze.

- All penstocks shall be of the non-rising spindle type.

- All penstocks shall be provided with one or more separate stainless steel emergency lifting wires for use in case of spindle brakeage. The wires shall be properly attached to the penstock door and led to operating level where the end of the wire(s) shall be provided with lifting eye(s) which shall be attached to a bracket.

- Penstocks shall be watertight under the conditions of head and flow direction they shall be designed for and exposed to.

- The penstocks shall be designed so as to secure tight closure while maintaining freedom of plate movement during operation and minimizing sliding wear of the sealing.

- Rubber sealing faces shall be formed from high quality synthetic rubber suitably shaped to interlock into groves in the frame or plate and shall be securely bonded thereto.

- Channel mounted penstocks shall be installed in recesses in the channel sides and grouted.

- In case that penstock width is greater than 2 m, penstocks shall be of double spindle type.

### Gate valves

Gate valves shall be of the double-flanged cast iron resilient seated full-bore type with vulcanised EPDM rubber on ductile iron wedge.

Gate valves from DN 50 mm to DN 300 mm shall be in accordance with DIN 3352 Part 4. The face-to-face dimension shall be to DIN 3202 Part 1, F4.

Gate valves DN 350 mm to DN 600 mm shall be in accordance with DIN 3352 Part 4. The face-to-face dimension shall be to DIN 3202 Part 1, F5.

Unless otherwise specified, each valve shall be provided with a suitable hand wheel of adequate diameter for the duty required. Gearing shall be supplied where necessary, to ensure that the required operating force applied by hand to the rim of the wheel does not exceed 250 N.

Gate valves of DN 500 diameter and bigger shall be motor driven.

Hand wheels shall have smooth rims and the direction of closing, which shall be clockwise, cast on them.

Valve stems shall be of EN 1.4021 stainless steel, machined all over with a machine cut robust trapezoidal or square form thread, operating in gunmetal nut.

Stem seals shall be the O-ring type with two such seals arranged for easy replacement of O-rings and shall be accessible for maintenance with the valve under pressure without removing the valve from service.

Fastening bolts shall be of stainless steel, countersunk and corrosion sealed.

Extended spindles for all motorized or actuator operated valves shall be provided with thrust tubes between valve and headstock in order to absorb the thrust in both directions of operation.

Valves shall carry identification plates or marks in accordance with appropriate standard.

All valves shall be painted in accordance with the specifications in item7.2 according to actual location.

All materials used in manufacture of the valves shall conform to the following minimum standards:

- Ductile Iron	DIN 1693 GGG-50

- Dezincification Resistant Brass	BS 2874 Grade CZ132 (EN 12167)

- Stainless Steel	DIN X 20 Cr 13

- O-rings	NBR Rubber.

Any standard, which fulfils the same functionality and describing the same quality level or better, shall replace any non-EN standards.

### Knife gate valves

Knife gate valves shall have face to face dimensions to EN 558-1.

Unless otherwise specified, knife gate valves shall be used for all sludge lines.

The body shall be made of cast iron. The gate and stem as well as connecting parts shall be made of stainless steel. Stem nut shall be of dezincification resistant brass.

Knife gate valves shall be painted in accordance with the requirements in item 7.2 according to actual location.

Materials for seals shall be suitable for use with wastewater.

Unless otherwise specified, each valve shall be provided with a suitable hand wheel of adequate diameter for the duty required. Gearing shall be supplied where necessary, to ensure that the required operating force applied by hand to the rim of the wheel does not exceed 250 N.

Knife gate valves of DN 500 diameter and bigger shall be motor driven.

Hand wheels shall have smooth rims and the direction of closing, which shall be clockwise, cast on them.

### Non-return valves

Non-return valves shall be normally closed, suitable for wastewater and shall open under minimum flow conditions. The non-return valves shall be of the swing type with lever and counterweight and position indicator.

The non-return valves shall be manufactured from cast iron with top hinged door.

The tightness of the non-return valves shall be secured with renewable accurately machined non-ferrous facing strips or with rubber sealing, which shall be easily renewable as well.

Valves shall be painted in accordance with the requirements in item 7.2 according to actual location.

All materials used in the manufacture of non-return valves shall conform to the following minimum standards:

- Cast Iron	EN 1561 Grade 220

- Gunmetal	BS 1400 Grade LG2 (EN 1982)

- Stainless Steel	BS 970 Grade 431 S29 (EN 10083)

Any standard, which fulfils the same functionality and describing the same quality level or better, shall replace any non-EN standards.

### Butterfly valves

Butterfly valves shall only be used at locations with no risk for rags, fibres etc. Use of butterfly valves for wastewater requires prior acceptance by the Project Manager.

Butterfly valves shall comply with EN 593 and be of the double flanged type with metal or resilient seating and grey or ductile cast iron body.

Valves shall be drop tight at closure and the diameter not less than that of the nominal pipe bore.

The disc shall be in grey or ductile cast iron with a resilient seating ring in moulded rubber, or other material to the approval of the Project Manager, located in a landing on the disc and secured by a gunmetal retaining ring fixed with screws made from homogenous corrosion resistant material.

The shaft shall be in one piece and attached to the disc by using fixings in a corrosion resisting material of a pattern which precludes the assembly becoming loose during service. Grub screws, pins or clamps shall not be accepted.

The shaft shall rotate in bearing bushes fitted with grease lubrication facilities.

Glands shall be of the O-ring type fitted on the operational shaft extension to the pressure side of the valve. The design shall be such as to facilitate O-ring replacement without removing the valve from service.

Unless otherwise specified, each valve shall be provided with a gearbox with hand wheel proportioned so that the required force applied by hand to the rim of the wheel does not exceed 250 N.

Butterfly valves of DN 500 diameter and bigger shall be motor driven.

The closing direction shall be clockwise and cast on the wheel.

Suitable stops shall be incorporated to prevent disc movements beyond the fully open and fully closed positions.

A valve position indicator to show the position of the disc shall be provided on the valve.

Valves shall carry identification marks or plate in accordance with EN standards.

All materials used in manufacture of the butterfly valves shall conform to the following minimum standards:

- Cast Iron	minimum GG 25 (EN 1561 Grade 220)

- Ductile (Sph. Graphite) Iron	minimum GGG 40 (EN 1563)

- Stainless Steel	minimum 1.4404 (EN 10083)

- Gunmetal	BS 1400 Grade LG2 (EN 1982)

- Seals and O-rings	EPDM or NBR.

Any standard, which fulfils the same functionality and describing the same quality level or better, shall replace any non-EN standards.

All butterfly valves and operation devices shall be painted in accordance with the requirements in item 7.2.

### Dismantling joints

A sufficient number of dismantling joints shall be incorporated in the pipe work in order to facilitate the exchange of bigger than DN 200 mm size or wherever necessary valves and armatures in the pipe work. The dismantling joints shall be made of GGG40 (ductile) sphero-cast iron and shall have an axial adjustment capability of at least  25 mm to facilitate easy dismantling and installation of pumps, valves, non-return valves, measuring devices, etc. Threaded rods and nuts through two opposite flanges shall secure the dismantling joint in the position determined during installation, so that the system represents a rigid connection of two adjoining pipes.

### Expansion joints

Expansion joints shall be used at the connections of the pumps and blowers to the pipelines.

Expansion joints shall be used also for air pipes on the aeration tanks against vibration and expansion of the air pipes.

Metallic Expansion Joints shall use in connections of the pumps and air pipes on the aeration tanks to prevent damage caused by thermal growth, vibration, pressure thrust and other mechanical forces.

Rubber Expansion Joints for connecting the blowers to the pipelines shall have a flexible connector fabricated from natural or synthetic elastomers and fabrics with metallic reinforcements designed to provide stress relief in piping systems due to thermal changes.

Expansion joints shall be having liner.

- Bellow Metarial: Stainless steel 1.4404 (AISI316L) or higher

- Connection Types: Floating Flanged

- Operating Temperature: -80/+200 C

- Operating Pressure: PN16/25/40/63 (as the case shall be)

- Nominal Diameters: DN25(1’’) –DN1000(40’’) (as the case shall be)

### Ball valves

The ball valves shall be of the two-way type and be provided with a handle for easy opening.

All flanges shall be rated and drilled for PN 10 according to DIN 2576 B or DIN 2632.

### Surge anticipating control valves, air relief and vacuum protection valves

Surge anticipating control valve, air relief and vacuum protection valve shall be new, have no material defect and, nominal diameter, nominal pressure and manufacturer's name shall be inscribed on.

#### Surge Anticipating Control Valve:

Surge anticipating control valve shall automatically protect the system against water hammers arising from powercut, power fluctuation and pump start-stops.

Surge anticipating control valve shall be installed in pump pressure side header and open to atmosphere. The bodies shall have Y-form so that pressure loss would be small.

Pilot-Actuator pressure signal for surge anticipating control valves to be used in waste water treatment plant and pump stations shall be provided from clean water resource equivalent to minimum operating pressure. A tank and a package pump unit shall be provided to enable surge anticipating control valve to operate properly.

Valve actuator part shall be double-chambered type.

Technical Features:

Body type:	Y-form

Actuator type:	Double-chambered diaphragm actuator

Control pilot:	Pressure-reducing pilot, pressure-fixing pilot

Connection type:	Flange connection

Maximum operation pressure:	16 bars

Body material:	min. GG40 ductile iron

Spring material:	min.1.4401 (AISI 316) stainless steel

Diaphragm material:	Neoprene rubber

Sealing parts:	1.4301 (AISI 304) stainless steel

Flap disk ring:	1.4301 (AISI 304) stainless steel

Seat:	Replaceable Buna-N material

Valve stem material:	1.4301 (AISI 304) stainless steel

Valve signal circuit:	1.4301 (AISI 304) stainless steel

#### Pressure Relief Valve:

Pressure Relief and air relief valves of suitable size shall be installed in top point of pressure line and header together with surge anticipating control valve. These valves shall be able to remove cavitation problems appearing when filling-discharging pipeline. This prevents constriction and flow reduction in pipeline.

Pressure relief valve having a wide orifice shall be able to provide necessary air while discharging the line (vacuum principle). Moreover, it shall have a mechanism preventing contact between wastewater and sealing elements of valve. The valve shall have the ability to evacuate compressed air and other gases while the pipe line is under pressure (air evacuation principle).

Technical Features:

Body type:	Double orifice

Connection type:	Flange connection

Minimum operation pressure:	0.2 atm

Maximum operation pressure:	16 atm

Valve body-bonnet material:	min. GG 25 cast iron

Body material:	St-37, St-37-2 carbon steel

Sphere material:	Polycarbonate copolymer

Sphere cage:	Polycarbonate copolymer

Seat:	Rubber

O-ring:	Buna-N material

Fittings:	Galvanized steel

Big floating ball:	1.4401 (AISI 316) stainless steel

Arm between floating ball and sphere:	1.4401 (AISI 316) stainless steel

### Telescopic valves

Open stem and yoke valve to be used to draw sludge from clarifiers, its pipes and parts shall be made up of 1.4404 (AISI 316L) stainless steel. It shall be used in sludge taking lines. It shall telescope up and down (two pipes, one inside other), having a proper diameter, depending on the flow rate of sludge taken. Sealing shall be provided between two pipes.

Telescopic valve shall be controlled by motor or manually. For manual control, wheel shall be installed in a suitable size, the turning force of which does not exceed 250 N. Wheel is approximately 1 meter above the platform. Closing direction shall be inscribed on wheels, preferably clockwise.

Motor driven valves shall have actuators which have 4-20 mA control signal.

### Electric actuators

Where required, penstocks and valves shall be operated by means of electrically driven actuators with integral reversing starters (EN ISO 5210). Each actuator shall be fully weatherproof to minimum IP55, and fitted with anti-condensation heater, upper and lower limit switches and torque switches, for operation through 4-20 mA signals. All power and control circuits shall have inside the actuator.

Each actuator shall be adequately sized to suit the application. The operating gear of all penstocks shall be capable of opening or closing the gate against an unbalanced head equal to the maximum working pressure.

The gearbox shall be oil or grease filled, and capable of installation in any position.

Alternative hand operation shall be possible, and the hand wheel together with a suitable reduction gearbox, if necessary, shall be of adequate dimensions for easy operation by one man. The motor drive shall be automatically disengaged when under manual operation. Hand wheels shall be rotated clockwise to close the valves or penstocks, and shall be clearly marked with the words "OPEN" and "CLOSE" and arrows in the appropriate directions. The rims of hand wheels shall have a smooth finish.

Control drives shall have a stall torque rating of at least 150 percent of the maximum required torque for the driven element, and shall be capable of operating at 65ºC continuously.  Stroking time to be suitable for application.

All drives shall have minimum repeatability of ±0.5 percent of full-scale travel.

All drives shall have slide wires or differential transformers and end limit switches for position and/or feedback control.

Electric drives shall have proportioned control.

All control drives shall include mounting stands, drive arms, clevises, connecting linkage and suitable enclosure.

### Pumps

Where applicable before delivery to site all pumps shall be works tested according to EN ISO 9906 witnessed by the Project Manager.

#### General

In each pumping installation, all pumps shall be equal with respect to manufacturer and type.

On the suction pipe before the pump an isolating valve shall be incorporated (only dry mounted pumps) and on the pressure pipe an isolating valve, dismantling piece and a check valve shall be incorporated (both dry and wet mounted).

All delivery pressure pipes from pumps shall be provided with connecting branch with ball valve and manometer.

For dry mounted pumps, the connection on both suction side and pressure side of the pump shall be via flexible connections.

Pipe connections of the pumps shall be made with flanges. Flange gaskets shall be of suitable material and shall be of the appropriate size. Flange gaskets shall be centered between flange bolts in such a way that they do not disrupt the flow section.

Single stage pumps with low-speed motors with speed below 1,500 rpm unless otherwise specified. For pumping of sludge, the speed shall not exceed this speed, whereas high speed pumps shall be accepted by the Project Manager under certain operational conditions for wastewater.

Multi-stage high-speed pumps shall not be allowed.

Pumps shall be arranged for priming by means of an adequate positive suction head in all possible operating conditions.

The operation cycle of the pumps shall include alternating also of the stand by pump. The pumps shall be dimensioned for minimum 10 starts per hour.

For centrifugal canal-wheel type pumps the maximum velocity at discharge flange shall be 3.5 m/sec.

Discernible noise caused by hydraulic turbulence and cavitation shall not be accepted.

Water hammers in the piping system shall be eliminated by installing surge vessels, special valves or similar.

The pump impeller shall be selected for maximum efficiency. Pumps shall operate right to BEP (Best Efficiency Point) at start conditions and so to the left of BEP at stop conditions.

The pump type shall be determined by the Contractor for the maximum time between failures (clogging etc.) which shall be a minimum of 60 operation days.

Impellers of minimum or maximum diameters in relation to size of pump house shall not be used.

Unless otherwise specified, pump housing shall be fabricated from cast iron and impellers shall be of wear and corrosion resistant steel as a minimum requirement.

When using frequency converters for speed control the pumps shall be equipped with external ventilation if speed control is possible below 35 Hz.

All pumps shall be equipped with thermal switches for thermal protection.

Pumps shall be easily accessible for service and provided slewing davits or cranes.

#### Submersible pumps for dry installation

The submersible pumps suitable for dry installation shall have the following features:

Design according to DIN 19569, where applicable.

Performance in excess of actual demand by at least 10% for flow or head.

Casing with large-flow cross-section and replaceable wear ring where applicable.

Impeller with large, unobstructed flow ways to ensure non-clogging and non-stringing operation

Impeller with means to reduce end thrust

Common motor/pump shaft supported in anti-friction bearings with grease and/or oil lubrication. Shaft not to be in contact with pumped medium.

Intake and discharge side of pump with flanged connection

Due to the dry installation of the pump, the motor cooling system shall be highly efficient. Cooling shall be based on indirect cooling for pumps ≥7.5 kW

Leaks seals shall be provided

Materials

The materials given below shall be the minimum requirements. The Contractor shall state in the appropriate sections the materials proposed by him.

volute casing:	min. GG-25 cast iron

impeller:	min. GG-25 cast iron or stainless steel 1.4301 (AISI 304) or higher

pump shaft:	min. C45 carbon steel or stainless steel 1.4301 (AISI 304) or higher

type of seal:	mechanical seal suitable for liquids with a high concentration of abrasive solids

Fastening components:	material stainless steel according to item 7.3.4

All electrical components as detailed under section “Electrical Power and Control Equipment”.

Drive

The motor shall have the following features:

dry-running three-phase asynchronous motor in watertight casing according to IEC standard

protection type IP 68

insulation class H

operating mode S3 or S8 (Frequency converter)

internal indirect cooling for pumps ≥7.5 kW

pump shall be equipped with cooling jacket for dry running application

moisture/water sensor device to prevent damage to motor windings and bearings

tandem mechanical shaft seal

thermo element in coil for motor protection

pump completely cabled.

motor efficiency class IE3

#### Submersible pumps for wet Installation

The submersible pump for wet installation shall have the following features:

Design according to DIN 19569, where applicable.

Performance in excess of actual demand by at least 10% for flow or head.

Casing with large-flow cross-section and replaceable wear ring where applicable.

Impeller with large, unobstructed flow ways to ensure non-clogging and non-stringing operation considering the media to be pumped.

Impeller with means to reduce end thrust.

Common motor/pump shaft supported in anti-friction bearings with grease and/or oil lubrication. Shaft not to be in contact with pumped medium.

Intake and discharge side of pump with flanged connection

The motor cooling system shall  be highly efficient.

Duck foot bend for automatic coupling of pump to discharge pipe.

Guide bar system for lowering/lifting of pump.

Fixing components.

The pumps shall be suitable for reversing by backflow in the pipe after pump stop.

Cable shrouds shall preferably be of steel wire mesh instead of synthetic material.

Materials

- The materials given below shall be the minimum requirements. The Contractor shall state in the appropriate sections the materials proposed by him.

volute casing	:	min. GG-25 Cast iron

impeller		:	min. GG-25 Cast iron or stainless steel 1.4301 (AISI 304) or higher

pump shaft	:	min. C45 carbon steel or stainless steel 1.4301 (AISI 304) or higher

type of seal	:	mechanical seal suitable for liquids with a high concentration of abrasive solids

fastening components, material stainless steel according to 7.3.4.

Drive

The motor shall have the following features:

dry-running three-phase asynchronous motor in watertight casing according to IEC standard

protection type IP 68

insulation class H

operating mode S3 or S8 (frequency converter)

internal cooling for pumps ≥7.5 kW

Pump shall be equipped with cooling jacket for wet running application

moisture/water sensor device to prevent damage to motor windings and bearings

tandem mechanical shaft seal

thermo element in coil for motor protection

sensor for bearing temperature

pump completely cabled

motor efficiency class IE3

#### Centrifugal pumps for dry installation

The centrifugal pump shall be suitable for dry installation and handling of liquids with long stringy solids as well as liquids of high solid concentration. The pump shall have the following features:

Design according to DIN 19569, where applicable.

Performance in excess of actual demand by at least 10 %.

Impeller with large, unobstructed flow ways to ensure non-clogging and non-stringing operationconsidering the media to be pumped.

Capable of pumping activated sludge and oil water mixtures.

Steep performance curve.

High efficiency.

Casing with replaceable wear liner.

Pump and motor on common base frame.

Pump shaft supported in anti-friction bearings with grease lubrication.

Pump with stuffing box packing.

Leaks seals shall be provided

Materials

The materials given below shall be the minimum requirements.

Volute casing	: min. GG-25

Impeller		: min. GG-25 Cast iron or stainless steel 1.4301 (AISI 304) or higher.

Pump shaft	: min. C45 carbon steel or stainless steel 1.4301 (AISI 304) or higher.

Drive

The drive unit shall shall the following features:

Dry-running three-phase asynchronous motor according to IEC-standard

Protection type IP 55

Insulation class F

Thermo element in coil for motor protection.

#### Progressive cavity pumps (Eccentric screw pump)

The eccentric-screw pump for conveyance of sludge shall have the following features:

Design according to DIN 19569, where applicable

Self-priming, rotary, valve less screw pump

Direction of rotation reversible

Suction chamber with venting and flushing attachment

Performance in excess of actual demand by at least 10 % for flow as well as head.

Anti-friction bearings with grease and/or oil lubrication

Type of seal: mechanical seal

Shaft at mechanical seal position to have wear resistant coating or wear sleeve

Sensor on suction side to prevent dry running

Pressure switch on discharge side

Pump and motor assembled on common base frame complete with coupling

All fastening material to be included

Pin-type/ball joints connecting drive and rotor to be greased for service life; gastight and watertight sealing.

Materials

The materials given below shall be the minimum requirements. The bidder shall state in the appropriate sections the materials proposed by him.

Casing:	min. GG 20 Cast iron or higher

Stator:	NBR, EPDM or Viton (wear resistant rubber)

Rotor:	chrome-nickel-molybdenum steel.

Seal:		mechanical seal (Suitable to process viscous product and with solids contents)

Drive

The drive unit shall have the following features:

three-phase asynchronous motor according to IEC-standard

protection type IP 55

insulation class F.

thermo element in coil for motor protection.

the speed of pump shaft shall not exceed 300 rpm

#### Rotary lobe pumps

The rotary lobe pump for conveyance of sludge shall have the following features:

Pump and gear motor group shall be assembled on hot dip galvanised steel base plate with coupling, protecting

diameter of solid particle: minimum 40 mm

shaft diameter: minimum 60 mm

Considering leaks shall occur during time through seals, the seals shall be maintained in a chamber sealed from exterior.  Pumps, which shall leak fluid to the external medium in case of a seal failure, shall not be accepted performance in excess of actual demand by at least 10 % for flow as well as head.

Maintenance and replacement of lobes and block seal shall be made through the front cover without requiring removal of pump suction and discharge line connections and/or coupling between motor and pump.

The bottom and top body parts of the pump shall be made in such way adjustable (movable) /replaceable against wears.

Materials

The materials given below shall be the minimum requirements. The bidder shall state in the appropriate sections the materials proposed by him.

body/front cover	: min. GG 25 Cast iron

shaft				: min. C45 carbon steel or chrome-nickel-molybdenum steel.

lobe				: helical shape, cast iron covered with NBR (minimum 3 wings).

pump sealing		: mechanical seal

wear plates		: Abrassion-resistant steel

Suction and discharge connections:  gooseneck shape with DIN 2633 as hot dip galvanized.

Drive

The drive unit shall have the following features:

three-phase asynchronous motor according to IEC-standard

protection type IP 55

insulation class F.

thermo element in coil for motor protection.

the motor power shall reserve at least 20% of its nominal power.

the speed of pump shaft shall not exceed 500 rpm at 50Hz.

The motors shall drive with frequency converters.

#### Grit, Grease and Scum Pumps

Type		: Vortex

Installation	: Submersible

rpm			: maximum 2900 rpm

Each pump shall be suitable for operation in a wet well installation, and shall be provided complete with duck food with automatic coupling, guide rails and lifting chain. For each grit pump shall be capable of handling wastewater containing grit settled on the bottom of grit chambers.

Each grit pumps shall be installed on travelling bridge and move with bridge. Each pump shall be provided with a stainless-steel pipe connected to the suction flange. Pumps shall have agitators. An agitator connected to pump shaft shall be provided after pump volutes. This agitator shall be durable against abrasive effect of the sand, coated with abrasit material.

Guide rails and lifting chain shall be made of stainless steel.

Each pump shall be provided with a control panel. The panel shall include an adjustable timer for setting the operation/pause times for the pump.

#### Dosing pumps

Chemical dosing pumps shall be of the plunger or diaphragm type driven by electric motors. Hydraulically actuated diaphragm pumps shall not be acceptable. Pump, motor and driving arrangement shall be mounted on a robust combined base plate incorporating a drain connection.

The operating rate of dosing pumps shall not be less than 6:1 for diaphragm pumps and 10:1 for plunger pumps, with overall accuracy within the following percentages:

|  | Diaphragm pumps | - Plunger pumps |
| --- | --- | --- |
| Accuracy of setting | 3 | 1 |
| Repeatability | 1.5 | 0.5 |
| Linearity | 3 | 1 |

Plunger pumps shall have alum-type-ceramic or stainless-steel plungers. Diaphragm pumps shall have thermoplastic diaphragms faced with polypropylene, butyl or polytetrafluoroethylene (PTFE). Pump heads shall be either stainless steel or polypropylene. Mechanical glands shall not be used.

The output of the pump shall be adjustable by varying the effective length of the stroke settings. Variable stroke mechanisms shall be incorporated which enable the pump is running by means of a micrometer hand wheel or similar device.

Pump motors shall incorporate an integral reduction gearbox drive, which shall be totally enclosed in a lubricated oil bath. The gearbox shall incorporate the cams for the plunger or diaphragm drive and shall be provided with oil filling and drain connections and visible oil level indication.

The design and location of metering pump heads shall facilitate easy dismantling for removal of any foreign matter.

Dosing pumps shall be provided with means for calibration by direct measurement upstream of the dosing pump. Manually isolated tapping shall be provided on the pump suction for connecting the calibration unit. The Contractor shall provide all necessary equipment and fittings in duplicate for the calibration of the dosing pump.

Particular attention shall be paid to the layout of the dosing pumps and pipework. All connecting manifold systems shall be permanent and complete with drain connections. When handling chemicals with low vapour pressure, piping shall be designed to eliminate vapour pockets. Dosing pumps shall be provided together with all accessories like back pressure valves as a complete set.

### Clamshell Grab Bucket

Clamshell grab bucket shall be used at Stone Trap to remove large objects from wastewater such as stones, woods etc. coming to the WWTP in heavy rain conditions.

The grab shall be perforated type to enable water drainage.

Operating system		: electro-hydraulic
Capacity				: 1 m3
Bucket jaws			: Abrassion-resistant steel with minimum 400 HB
Grab plate			: St 44
Grab frame			: St 44
Arms				: St 52-3
Shaft mills			: C 1050 bronze bushing with grease lubrication
Painting				: 2-layer anti-corrosion

### Coarse screens

Screen type:					Automatic screen

Bar spacing:					30 mm

Bar thickness:					approx. 10 mm. Bar thickness shall be chosen as strong enough to withstand the pressure acting due to accumulation of screenings as well as to maintain low pressure loss.

Material (parts in contact with media):	 Stainless steel EN 1.4404 (AISI 316L)

Coarse screens where solids harmful to the inlet pumps shall be retained shall be installed.

The automatic coarse screens and all equipment related to the screen facilities shall be kept in operating working conditions during frost.

If required head shall be available, an overflow bypass to the receiving water shall be established upstream of the coarse screen.

The individual coarse screens shall be able to isolate by means of penstocks or similar to allow service of each of the individual coarse screens.

The screen operation shall be controlled by means of a level transmitter installed upstream the screens. The automatic screens shall be provided with an automatic release system in case of stuck moving parts.

The screens shall be secured against overload.

The screens shall be manufactured completely of stainless steel EN 1.4404 (AISI 316L).

Chains and sprockets (if used) shall be special hard steel with surface hardening treatment to avoid wearing and deformation of chain links and sprockets.

The automatic screens shall be able to be maintained and inspected when installed.

Human contact with screenings shall be minimized, i.e. screenings shall be conveyed automatically to the reception container located at ground level.

The screenings from the coarse screens shall be transferred to a reception container through belt type conveyor.

If the screenings conveyor is out of order the screens shall be able to operate without. The discharge height of the screens shall be sufficient to allow screenings to be dropped directly into a reception container.

The screens and screen containers shall be located in a building and the screen and building shall be ventilated.

Easy access to all mechanical equipment shall be provided.

### Fine screens

| Screen type | perforated plate type screen |
| --- | --- |
| Perforation spacing | perforation 6mm for perforated plate screens |
| Material (parts in contact with media) | Stainless steel EN 1.4404 (AISI 316L) |
| Screen elements | Stainless steel EN 1.4404 (AISI 316L) or polyamide |

The screen operation shall be controlled by means of a level transmitter installed upstream the screens.

The automatic screens and all equipment related to the screen facilities shall be located in a building.

Combined press and washing unit shall be provided together with the fine screen.

The automatic screens shall be provided with an automatic release system in case of stuck moving parts.

The screens shall be secured against overload.

The screens shall be manufactured completely of stainless steel EN 1.4404 (AISI 316L).

Chains and sprockets (if used) shall be special hard steel with surface hardening treatment to avoid wearing and deformation of chain links and sprockets. No chain, bearings or any devices for transmission shall be allowed to be submerged unless they are specially designed to work under wastewater.

The automatic screens shall be able to be lifted up of the inlet channel for repair and inspection by means of build-in hinges. Furthermore stop logs or penstocks shall be provided to enable isolation of the automatic screens for maintenance.

The screenings from the fine screens (if not combined) shall be transferred to screen press through screw type conveyor. Screen press shall be spiral conveyor type with washing compacting facility.

### Conveyer systems

For transportation of screening, sand, sludge etc.

#### Spiral-conveyer

Shaftless spiral conveyer.

The screw conveyor with washing and compacting facility shall be capable of transport, wash and compact the screenings discharged from the screens. Wash water shall be treated wastewater, see item7.8.46. Treated Wastewater for Reuse. Reject water from the compacting/washing facilities shall be led into the screen channel or inlet pump sum.

Design due to circumstances required; incl. anti vibration supports, trough with connection flange, feeding and discharge chute.

Materials: In accordance with the material to be transported, but shall meet at least following specifications:

- Materials for support legs, suspension, cover and trough shall be stainless steel EN 1.4404 (AISI 316L or higher),

- Trough lined with PEHD not less than 8 mm thick

- Spiral (screw) made from min. St-52 carbon steel with epoxy painted or EN 1.4404 (AISI 316L) or higher stainless steel.

The shaftless spiral conveyer shall be manufactured in its full length. Site welding of the conveyer shall not be acceptable.

Motor:

Protection class IP 55 with thermo protection.

Insulation class: F

#### Belt conveyers

Mainly consisting of support and frame with sound absorbing, oil and sewage resistant bearings, oil and sewage resistant belt with plies of fabric or EPDM; incl. motor.

Completely encased to avoid odour nuisance. Belt velocity shall  be chosen according to required capacity but not exceed 0.5 m/sec.

Number and distance of roller due to duty required. At feeding zone distances shall  be reduced.

Side plates to be equipped with rubber or plastic aprons at contact area to belts.

The specified width of the conveyer shall be the required effective width of the conveyer belt. The inclined sides of the belt and the conveyer frame shall be in addition to the specified with of the conveyer.

Bearings shall be sufficiently rated for both vertical and horizontal loads.

Material: Frame, supports, enclosure, baffles, side curtains (plates) and inlet and outlet chutes: EN 1.4404 (AISI 316L) stainless steel.

All other parts: cast iron, hot dip galvanised steel or steel with corrosion protection according to general specifications.

Bolts: A4

Motor:

Protection class IP 55 with thermo protection.

Insulation class: F

### Drum Sieve

Floated grease and surface scum/sludge which is scraped off from the grit & grease removal tank shall be conveyed to externally or fed drum screen. Screening shall be performed by bars which have triangle cross section or perforated plate. Particles bigger than 1 mm. shall be hold in the drum screen.

Drum screens shall have a pressurized spray cleaning system. Retained particles shall be conveyed to container via scraper (or spiral conveyor).

Equipment shall not have dewatering section.

Drum screens shall have inlet / outlet / overflow connections. Overflow and screened wastewater shall be directed to plant inlet. Drum screens shall be located inside a building in frost free conditions. To avoid odour nuisance the equipment shall be covered and connected to odour treatment system.

Materials;

Drum 					: Stainless Steel (EN 1.4404)

Frame 					: Stainless Steel (EN 1.4404)

Wash water pipes / nozzles 	: Stainless Steel (EN 1.4404)

Drive Unit				 : GG25

Easy access to equipment for maintenance purposes shall be ensured.

### Screenings press

The screen press trough and cover shall be made of stainless steel EN 1.4404 (AISI 316L) plate. The trough shall be provided with an anti-friction lining of PEHD, not less than 8 mm thick. The screw shall be of the shaft-less type and made of special steel. Operating range of screen press, fine screen and conveyor bands shall be adjustable via PLC system. Spiral edges of screen press shall be furnished with brush against sticky dirts.

If the washing and compacting unit is out of order the screen shall be able to operate without these auxiliary units. The discharge height of the screen shall be sufficient to allow screenings to be dropped directly into a reception container.

An emergency bypass, for bypassing the automatic screen, shall be installed.

The washing and compacting section and all bolts, screws, pipes for compressed screenings, supports and brackets shall be of stainless steel EN 1.4404 (AISI 316L) in accordance with the specifications for stainless steel.

Easy access to all mechanical equipment such as screens, gates and washing and compacting unit shall be provided.

Drain-off facilities shall be provided where necessary. Pipes for compressed screenings shall be removable for easy cleaning.

Operation of screens, washing and compacting unit to be controlled by the difference in water level up- and downstream the screen superseded by timer control.

### Grit and grease removal equipment

The aeration equipment shall provide coarse bubble, clogging free aeration. The diffusers shall be easy dismountable section-wise without emptying the tank.

The scrapers for grease removal shall operate timer controlled. The grit chamber aeration shall be continuous. Each drop air pipe shall be provided with a shut off valve.

Easy access shall be provided to all equipment that needs regular service and maintenance.

All submerged steel shall be stainless steel EN 1.4404 (AISI 316L).

The inflow shall be distributed equal to all lines.

The grit- and grease installation shall include service penstocks for closing each line. A penstock shall be installed before and after each line for isolation of the line.

A separating wall shall be constructed between sand channel and grease channel using grease lamellas made up of wooden and polyethylene material. Those lamellas shall be of 2.5-3.0 cm thickness and 10 cm width. The construction holding of lamellas shall be of stainless steel EN 1.4404.

Electrical panel of equipment shall be provided as stainless steel and IP65.

Travelling Bridges for Grit and Grease Chambers

Travelling bridges for grit and grease chambers shall be complete units consisting of a bridge with surface scraper for the collection and removal of grease from the surface of the grease chamber.

The bridge shall be a lattice construction made of min. St 37 carbon steel with walkway of grated floor panels and hot dip galvanized after fabrication.

The surface scraper shall collect and convey the grease to the weir at the outlet end of the Grit and Grease Chamber. The scraper shall be mechanically lifted out of the water and locked in its top position when the bridge approaches the weir. The scraper shall remain in its top position while the bridge returns to the inlet end where the scraper shall be released automatically.

The travelling bridge shall be controlled from a local panel installed on the bridge. The bridge and the grit pump shall operate automatically; however it shall be possible to operate the bridge and the grit pumps manually from the panel.

Surface scraper, sand and grease pump installation materials, and slipway pipes shall be of EN 1.4404 (AISI 316L) stainless steel.

The power supply to the bridge shall be provided through a flat cable running in a guide rail along one side of the Grit and Grease Chamber wall.

The bridge shall be provided with bogies and two wheels at each end running directly on the rails installed on the concrete walls. The material of rail shall be GG 60 cast iron and the material of wheels shall be St-37 carbon steel.

One wheel at each end shall be connected to a drive unit via traversing drive shafts. Furthermore, the bridge shall be provided with four fixed guide wheels running on the inside of the walls. The guide wheels shall ensure that the bridge runs evenly.

The scraper shall be provided with the necessary gear box, drivers, motors and supporting bridge structures.

The bridge shall be walkable, and covered with galvanized open mesh flooring and provided with railing.  The bridges shall be stiffened by cross and diagonal steel members be provided with sub-frames to carry the electric drive and cable drum and be designed for a load of 1.5 kN/m² and the deflection shall not exceed 1/500 (according to DIN-EN 19569).

### Diffusers in grit chambers

Diffusers for aeration of the grit chamber shall be perforated tubes of stainless steel EN 1.4404 (AISI 316L) for coarse bubbles. Perforated air pipes shall be provided together with necessary installation materials for air pipes. Perforated air pipe sizes, quantities and hole diameters shall be calculated by the Contractor.

Each of the air supply pipes to the diffusers shall be provided with shut-off valves.

The air distribution pipes both submerged and not submerged shall be made of stainless steel EN 1.4404 (AISI 316L).

Stainless steel shall be in quality according to specifications for stainless steel.

It shall be possible to dismantle a diffuser and take it up for inspection and maintenance without the need of emptying the tank.

### Grit classifier

In grit washing plants the organics are separated from the mineral particles. (Remaining less than 3 % organic content)

After removal of the organic material in grit washers the clean grit is removed through a classifying screw, statically dewatered and discharged into a container.

For sedimentation of easy settle-able substances of the sand water mixture withdrawn from the grit chamber. The grit classifier shall be with funnel shaped inlet for sedimentation with sand discharge by screw.

Required grade of separation:	> 90% for particles  0.2 mm;

Design to guarantee that separated matters shall not harm or damage the separator (over load safety device).

The classifier shall be made from stainless steel EN 1.4404 (AISI 316L), conveyer coated with polyethylene, screws made from special steel or stainless steel.

The feeding rate shall be designed to match to sand pump capacity.

To avoid odour nuisance the complete plant shall be housed and if necessary ventilated.

The grit classifier and container shall be located inside a building in frost free conditions.

### Containers for screenings and grit

The containers for screenings and grit classifier shall be provided. The containers shall be equipped with a hinged lid. In general construction and design, the containers shall be compatible with TSE and DIN 30720 standards and shall be made from St 37 carbon steel sheet and dipped galvanized material with a minimum thickness of 5 mm.

Containers shall be fitted with wheels for easy manually handling. It shall be compatible with the End Recipient's existing containers and trucks. The End Recipient's opinion shall be taken when determining the type of the containers.

Containers shall have drainage to drains filtrate water with blind flange. Drainage pipe shall be connected to appropriate place. Capacity of containers to be supplied for each WWTP units shall have 5 m3.

The containers shall be enclosed and hinged covered (opening / closing) so as to prevent the spread of unpleasant odours around the environment.

### Submersible mixers

Generally, the mixers shall be of the submerged rotating propeller type. The mixers shall be mounted on guide bars, which allow them to be lifted from the tank for inspection and maintenance. A removable crane with steel wire winch on an individual basis shall be provided for the hoisting of each mixer.

Mixers shall be provided with PT100 sensors in the windings for thermal protection. Furthermore, mixers shall be provided with leak detectors. Relevant relay including PT100 and leak contacts shall be provided.

Mixers shall be corrosion protected according to item 7.2 .

The mixer system shall be complete with a local switch panel with emergency stop push button, On/Off-key-switch, Manual/O/Automatic-switch, manual operated lifting and lowering device, guide rails, lifting cable / chain. Guide system incl. brackets and fixing parts shall be made of stainless steel EN 1.4404 (AISI 316L). Hand operated cranes shall be delivered in stainless steel EN 1.4404 (AISI 316L). Bottom fixations for winches shall be made of stainless steel EN 1.4404 (AISI 316L), winch itself which do not have a contact with liquid shall be stainless steel EN 1.4404 (AISI 316L).

Special attention shall be paid to the design and construction of the panels taken into consideration the particular climate conditions with high temperatures and up to 100% humidity.

The mixers shall be equipped with stainless steel or glass fibre reinforced polyurethane blades with self-cleaning hydraulics. Mixer and drive motor shall be submerged in the media and of protection class IP68 with insulation class H, minimum 80% efficiency, leakage control and mechanical seals. The mixers shall ensure that the content of sludge in the water is kept in constant suspension. Maximum allowed deviation of sludge concentration measured at different levels and spots in the process tank shall be average 5%.

For mixers in raceway shaped tanks the average velocity in the process tank shall be at least 0.30 m/s (when the diffusers are in the operation).

The mixers for raceway tanks shall be of the slow rotating type with a maximum permitted peripheral velocity of 7 m/s and propeller speed at maximum 50 rpm.

Mixers for different shapes of tanks where no velocity as such but only turbulence shall be obtained the mixer shall be of the high-speed rotating types.

Stainless steel shall be in quality according to specifications for stainless steel.

Sealing Motor Cast-in cable flange EN-GJS400, longitudinally water tight, cable plug-in connection in motor chamber mechanical seal propeller side mating of material silicon carbide / silicon carbide mechanical seal motor side mating of material hard carbon / silicon carbide common water seal made of paraffin oil.

Material:

Casing motor-gear:	min. GG25

Propeller:			Stainless Steel EN 1.4404 (AISI 316L) or higher / Glass fibre reinforced polyurethane

Propeller shaft:		Stainless steel (EN 1.4021 – AISI 420)

- Protection type: 		IP 68

- Insulation class: 		H

Bolts and nuts:		A4

These material examples shall describe the minimum required qualities.  The contractor is free to offer other materials with the same or better quality which acceptance shall be subject to the Project Manager. The bearings are to be sized to guarantee a service life of 100,000 hours according to ISO and AGMA norms.

For easy service moveable cranes fitted with winch shall allow easy lifting and lowering of each mixer. One crane for each mixer shall be provided. Cranes shall be manufactured of either aluminium or stainless steel EN 1.4404 (AISI 316L). The wire shall be of stainless steel EN 1.4404 (AISI 316 L).

The Contractor shall be full responsible for the design, choice of material and equipment, delivery to the site and installation of all. And also, the Contractor shall submit CFD analysis reports for only biological process tanks, all the layouts, calculations, and equipment performance curves with the own design.

### Blowers

#### Positive Displacement Blowers

Blowers shall be of the positive displacement lobe type (roots type) and controlled via frequency converter.

The blowers shall supply both grit chamber as well as other facilities such as air lift pumps. Capacity of the blowers shall be determined by the Contractor.

The blowers shall be operated alternating.

The motors shall be provided with bimetal "klixon" / PTC or PT100 sensors for thermal protection.

The blowers shall be provided with silencer at inlet and outlet and noise reducing covers. Noise level shall not exceed 85dBA 1 m away from the blower inside the station. Noise reduction covers shall permit easy dismantling and mounting for maintenance and repair and if necessary, facilitated with internal ventilation.

The speed of blower shall not exceed 3000 rpm.

When selection of blower types it shall be considered that some types of blowers emit pulsations at the discharge that might be transferred to the air distribution pipes with noise problems as consequence.

Noise shall be limited to a minimum and not exceed the requirements at the field boundary according to requirements stated in the Employer's Requirements, Document No 1: Design Basis.

Pipes inside the blower station shall be of stainless steel EN 1.4404 (AISI 316L). Each blower shall be provided with all necessary instrumentation and valves such as: check-valves, blow-off valves, pressure gauges on suction- and discharge side, shut-off valves as well as a flexible connection to the pressure manifold.

Lead-in pipes shall be designed to prevent possible damages to the pipes or concrete caused by vibrations and thermal expansions.

Distribution pipes outside the blower building shall be buried and buried pipes shall be made of stainless steel EN 1.4404 (AISI 316L) quality according to the requirements stated for stainless steel.

The requirements for air velocity are stipulated in the Employer's Requirements, Document No 2: Plant Description.

Air intake to the blower station shall be provided with a filter, which in degree of purification corresponds to the requirements of the diffusers.

The blowers shall be of the rotary piston type, based on the roots-compressor-principle and shall be manufactured in accordance with DIN 1945 with an admissible tolerance of +/-5%, referred to the power consumption and the intake volume.

Two rotors shall be located inside the housing. The housing shall be provided in cast iron, material GG20, with cast-in pre-inlet channels in the discharge side cylinders part to minimize the sound by pulsation reduction.

The rotors shall be dynamically balanced (with test certificate) and manufactured in carbon steel, C45, drop-forged in one piece.

The helical timing gears, material 16 MnCr5, shall be teeth hardened and ground, and machined to the highest precision.

The sealing at the conveying chamber shall be by three piston ring labyrinth seals and oil slingers. The sealing at the driving shaft shall be by radial sealing.

Each retain piston blower shall be covered by an acoustic hood of galvanized steel plate in segmental design with hardly inflammable internal lining.

Each blower shall be provided with the following components:

a.	base frame with integrated absorption - silences, including console and tension device for motor.

b.	1 set of anti-vibration mountings including holding down bolts.

c.	1 intake filter silence and 1 discharge filter silencer.

d.	V-belt drive with guard.

e.	1 pressure relief valve.

f. 	1 connection housing with fitted non-return valve and connecting flange for pressure relief valve.

g.	Flexible connection with hose clamps.

h.	1 pressure gauge with connection places.

i.	1 vacuum indicator for filter control.

j.	1 driving motor, 1EC standard, design B, 3 phases, protection IP 54, size 132S, insulation classification B.

#### Centrifugal/Turbo Blowers

Blowers shall be centrifugal type, magnetic bearing or air bearing and controlled via frequency converter. If a magnetic bearing blower is selected, it shall have a control unit that holds the deviations of the shaft in balance.

The blower station shall be able to provide air linear in the minimum range of 20% to 120% of required maximum design capacity in terms of flow to the biologic reactors at the actual conditions. Each blower shall operate linear in a range of 45% - 100% of its maximum capacity. Actual conditions are in terms of discharge pressure, ambient temperature range and ambient humidity and altitude at the Site.

The efficiency of the blowers shall be no less than 80% through the entire duty range. The maximum efficiency in the duty range shall be no less than 85%.

Capacity of the blowers shall be determined by the Contractor.

The blowers shall operate fully automatic based on a pre-set oxygen value, monitored in the biologic reactors.

Blowers shall operate alternating.

The motors shall be provided with bimetal "klixon" switches or PT100 sensors for thermal protection.

The blowers shall be provided with silencer at inlet and outlet and noise reducing covers. Noise level shall not exceed 85dBA 1 m away from the blower inside the station. Noise reduction covers shall permit easy dismantling and mounting for maintenance and repair and if necessary, facilitated with internal ventilation.

Pipes inside the blower station shall be of stainless steel. Each blower shall be provided with all necessary instrumentation and valves such as: suction filter, pressure relief-valve check-valves, blow-off valves, pressure gauges on suction- and discharge side, inlet filter clog indicator, shut-off valves as well as a flexible connection to the pressure manifold. Lead-in pipes shall be designed to prevent possible damages to the pipes or concrete caused by vibrations and thermal expansions.

Distribution pipes outside the blower building shall not be buried.

The requirements for air velocity are stipulated in the Employer's Requirements, Document No 2: Plant Description.

Air intake to the blower station shall be provided via a filter, which in degree of purification corresponds to the requirements of the blower and aeration diffusers.

The building housing the blowers shall be adequately ventilated to prevent overheating. If air intake is from inside the room, adequate unlock able ventilation ducts e.g. louver openings, shall prevent vacuum creation.

#### Factory Acceptance Test of Centrifugal/Turbo Blower

Prior to dispatch from the works, the turbo blowers are subjected to factory acceptance test (FAT) under load and the operational, output and consumption data described in the following documented in a test protocol. Such protocols serve as proof of specified technical performance. If so desired, the test run of the blowers shall be carried out in the presence of the Project Manager.

The following values shall be to be recorded in a test protocol during the test run of each blower (measurements at load points 100%, 75%, 45% according to ISO 5389 and VDI 2045):

Air intake

(273 K, 1.013 bar abs.)	: m3/h

Air outlet temperature	: 0K, 0C

Air flow control range	: %

Differential air pressure	: bar

Power requirement	:kW
Efficiency	: %

The following points shall be documented in the acceptance protocol:

Determination of the completeness of the delivery

Determination of the provision of inventory documents, operating instructions and maintenance schedules

Verification of the efficiency and capacity of the blowers

### Aeration diffusers for the activated sludge tanks

Aeration in process tanks shall be based on floor mounted diffusers with fine bubble diffusers.

The aeration diffusers shall transfer the oxygen content in the compressed air to the sludge/water-mixture in the bioreactors as efficient as possible. Minimum oxygen transfer coefficient (SSOTE) shall be 16 g O2/Nm3 at standard conditions according to DIN EN 12255-15 in clean water at 20°C.

On demand by the Project Manager the efficiency shall be verified in a test with pure water for the selected aeration system in accordance with an expert to be chosen by the Project Manager. Test shall be carried out on site in one basin (to be chosen by the Project Manager).

The design capacity per diffuser in Nm3/h shall be equal or lower than 75% of the tolerable maximum capacity in permanent operation. In order to minimize the power consumption maximum pressure, drop over the diffusers at maximum design air flow one year after commissioning shall not exceed 0.5 mWC.

The drop legs shall be made of stainless steel (EN 1.4404) according to specifications for stainless steel up to water level in the tank and rest of pipe shall be made of HDPE PE 100 PN 16. The immersed distribution pipes shall be made of HDPE PE 100 PN 16. Manifold pipes and header pipes shall be made of HDPE PE 100 PN16. The support system of the distribution pipes shall be made of stainless steel (EN 1.4404).

Necessary valves on the pipes for air distribution to shut-off and adjust the airflow of each section shall be included. Arrangements for collection and drain-off of condensed water from all possible spots condensed water is expected to accumulate shall be built in as part of the aeration diffusers.

The airflow to each tank shall be regulated relative to the oxygen content in the water. The airflow shall be automatic regulated by means of motor operated butterfly valves installed at the air supply pipe from the corresponding blowers.

Diffusers shall be either tube- or disc type. The diffuser material shall be resistant to the environment they are exposed to in the present bioreactor. If bioreactors shall be run in alternating operation diffusers shall be rated for this without clogging.

### Aeration diffusers for the aerobic digesters

- Diffusers in the aerobic digester tanks shall be based on floor mounted diffusers with coarse bubble diffusers.

- The coarse bubble diffusers shall be clog - free design and the material of the diffuser body shall be either 1.4401 or PVC or CPCV with resistant to temperature, corroison and UV.

- On demand by the Project Manager the efficiency shall be verified in a test with pure water for the selected aeration system in accordance with an expert to be chosen by the Project Manager. Test shall be carried out on site in one basin (to be chosen by the Project Manager).

- The design capacity per diffuser in Nm3/h must be equal or lower than 75% of the tolerable maximum capacity in permanent operation. In order to minimize the power consumption maximum pressure, drop over the diffusers at maximum design air flow one year after commissioning shall not exceed 1 mWC.

- The drop legs shall be made of stainless steel (1.4404) according to specifications for stainless steel. The immersed distribution pipes can be made of HDPE or PVC. If PVC pipe is used minimum tensile strength of 7000 PSI shall be required. SDR sewer pipe is not acceptable for any in-tank piping. Factory solvent-weld all PVC joints.  Field solvent welding is not permitted. Manifold pipes and header pipes shall be made of either stainless steel (1.4404), Sch40 wall thickness PVC or HDPE. The support system of the distribution pipes shall be made of stainless steel (1.4404).

- Necessary valves on the pipes for air distribution to shut-off and adjust the airflow of each section shall be included. Arrangements for collection and drain-off of condensed water from all possible spots condensed water is expected to accumulate shall be built in as part of the aeration diffusers.

- The airflow to each tank shall be regulated relative to the oxygen content in the water. The airflow shall be automatic regulated by means of motor operated butterfly valves installed at the air supply pipe from the corresponding blowers.

### Scraper bridges for the clarifiers

The scraper bridge to be used for circular clarifiers shall be half bridge. The scraper bridges inclusive of bottom scraper and surface scraper shall spans from the centre of the tank to the wall. Scraper bridges for circular tanks shall be designed as self-supporting lattice structures fabricated of steel sections and provided with walkway of open mesh flooring. The bridge shall be provided with main bearing in the centre of the tank, mounted on a cross member of steel, which rests on four concrete columns. A geared motor provided with a driving wheel shall drive the bridge. The bridge shall be fitted with a boogie with wheels that runs on the top of the outer wall of the tank. The bridge shall be easy and safe to push to the position wanted, and uninterrupted could rotate all 360°. At the periphery of the tank, the bridge shall run on two wheels with rubber tyre. A gear motor shall drive one of the wheels. The peripheral speed of the scraper shall for clarifiers be 1.8 - 2 m/minute.

The drive motors shall be provided with power from a control panel mounted on the bridge. The panel shall be powered from the centre structure of the tank via a collector ring mounted on the bridge.

The bridge shall be provided with bottom scraper for collection and transport of sludge to the sludge pit in the centre of the tank. Furthermore, the bridge for secondary clarifier shall be provided with a surface scraper for collection and transport of floating sludge to a floating sludge funnel at the tank periphery. The bottom scraper arms shall be arranged for inspection and replacement of blades and blade tips. For the cleaning of the effluent trough and scum board the bridge shall be furnished with a rotary brush.

The bridge inclusive of open mesh floor sections and steel cross members shall be hot dip galvanized steel in accordance with specifications in Corrosion Protection in item 7.2 of the Employer's Requirements.

Bottom scraper, surface scraper, floating sludge arrangement and all suspensions and brackets shall be fabricated of stainless steel EN 1.4404 (AISI 316L). Stainless steel shall be in quality according to specifications for stainless steel.

Geared motors and not galvanised steel items not immersed shall be adequately protected against corrosion. Such items shall be corrosion protected according to Corrosion Protection in item 7.2 of the Employer's Requirements.

The bridge shall be designed to carry a uniform load of 1.5 kN/m2 in addition to dead weight and operational loads. The Contractor shall design the bridge for the actual point-load adequate for the equipment to be unloaded, however, no less than 3.0 kN in the middle of the span.

The maximum allowable deflection at the above design loads shall be 1/500 (Acc. To DIN-EN 19569) of the span. Limitations of the load bearing capacity of bridge shall be indicated on a distinct sign mounted at the entrance to the bridge.

The width of the bridge shall not be less than 800 mm. The height of the handrails shall be minimum 1000 mm. All open mesh floor sections forming the walkway of the bridge shall be properly secured against skidding by means of special brackets. The bridge shall be furnished with toe plates.

The centre bearing shall be adequately rated for continuously operation under the maximum design load.

Lubrication points for the centre bearing shall be easily accessible without the necessity of dismantling any floor sections.

The centre bearing shall be fitted with an arrangement of slip rings with adequate amount of slip contacts rated for 16 Amperes to provide all motors etc. with power plus one contact for earthing. A set of surplus 3 (three) slip contacts for spare purpose shall be included. The arrangement shall be safely internal fitted in a protective capsulation. The arrangement shall be well constructed by design and chose of materials to prevent corrosion, condense and development of ice that shall disturb the operation.

The bottom scraper shall span over the entire tank radius, and be designed for effectively collection and transport of settled sludge to the sludge pit in the centre of the tank. The bottom scraper shall be provided with a sufficient number of wheels and fit perfectly to the bottom of the tank.

The surface scraper shall ensure collection and transport of floating sludge via screw conveyer system, chain track system or any other system which shall remove floating materials to scum well located at deflector by force. The surface scraper shall span over the entire tank radius and be designed to convey the floating sludge towards the periphery of the tank.

A geared motor of recognized make shall drive the rotary brush. The brush shall be adjustable and lockable in desired positions during operation. The mechanism shall be made of stainless steel EN 1.4404 (AISI 316L). Springs and pulleys shall be made of stainless steel EN 1.4404 (AISI 316L).

Electrical panel of equipment shall be provided as stainless steel and IP65.

### Effluent troughs, baffles, stengel and scum boards for clarifiers

Steel inboard weir troughs shall be designed with adjustable effluent weirs. Heavy fabricated knee braces anchored to the concrete wall shall individually support all segments.

Weir plates shall be furnished for mounting on the effluent troughs. Slotted holes for mounting shall be provided in the weir plate to provide vertical adjustment. The weir plates shall have 90° V-notches. The number of V notches shall be determined by the Contractor.

Effluent weirs, baffle segmental troughs, stengels and circular scum baffles for clarifier tanks with supports and anchorage shall be fabricated of stainless steel EN 1.4404 (AISI 316L). The minimum plate thickness allowed shall be 3 mm.

Stainless steel shall be in quality according to specifications for stainless steel.

### Service bridges for circular tanks

Service-bridges for circular tanks shall be designed as self-supporting lattice bridge fabricated of steel sections and provided with walkway of open mesh floor. The bridge shall be provided with a main bearing in the centre of the tank, assembled on a centre-suspension resting on 4 columns of concrete. The bridge shall be fitted with a boogie with wheels that runs on the top of the outer wall of the tank. The bridge shall be easy and safe to push to the position wanted, and uninterrupted could rotate all 360°. An efficient brake system shall be provided to ensure no unintended travelling of the bridge is possible.

The bridge supporting members and open mesh floor sections shall be hot dip galvanised in accordance with specifications stated in Corrosion Protection, item 7.2.

The bridge shall be designed to carry a uniform load of 1.5 kN/m2 in addition to dead weight and loads during. The Contractor shall design the bridge for the actual point-load adequate for the equipment to be unloaded, however, no less than 3.0 kN in the middle of the span.

Maximum allowed deflection by rated load shall be 1/500 (Acc. To DIN-EN 19569) of the span.

The width of the bridge shall be as minimum 800 mm.

Bridges shall be provided with necessary hoisting equipment for e.g. haul up and reinstall diffusers and mixers etc. Bridges and equipment shall be rated and designed to allow all haul ups and reinstallation of equipment as well as its inspection and maintenance shall be carried out safe and unburdened, and without requirements for heavy lifts.

The centre bearing shall be rated for at the rated load including the operational load.

### Service bridges for process tanks

Service-bridges in steel for process tanks shall be designed as self-supporting bridge fabricated of steel sections and provided with walkway of open mesh floor.

The bridge supporting members and open mesh floor sections shall be hot dip galvanised in accordance with specifications stated in Corrosion Protection, item 7.2.

The bridge shall be designed to carry a uniform load of 1.5 kN/m2 in addition to dead weight and operational loads. The Contractor shall design the bridge for the actual point-load adequate for the equipment to be unloaded, however, no less than 3.0 kN in the middle of the span.

Maximum allowed deflection by rated load shall be 1/500 (Acc. To DIN-EN 19569) of the span.

The width of the bridge shall be as minimum 1000 mm, adequate for transporting equipment from tanks to the ground.

Bridges shall be provided with necessary hoisting equipment for e.g. haul up and reinstall diffusers and mixers etc. Bridges and equipment shall be rated and designed to allow all haul ups and reinstallation of equipment as well as its inspection and maintenance shall be carried out safe and unburdened, and without requirements for heavy lifts.

### Dewatering equipment - mechanical decanter

#### Decanter Centrifuges

The centrifuges shall be the type of bowl and work horizontally. The sludge cake shall be transported with a conveyor system in a rate depending upon the velocity of centrifuge. Scroll / bowl velocity difference shall be illimitable changeable and shall be controlled with PLC. The centrifuges shall be driven by means of an electrical motor and V belt and constructed as a packaged set, consisting bowl and screw electrical motors. The connection between centrifuges and motors shall be created with frequency converters. Panels, wires and mounting belong to centrifuges.

The Decanter-Centrifuge shall be constructed as a packaged unit, consisting of but not limited to the following components:

- a rotating bowl and scroll assembly

- a drive system

- a foundation

- rotor and motor covers

The bowl shall be imbedded in heavy-duty bearings which are mounted in the foundation. The bowl bearings shall be grease lubricated.

The bowl shall consist of a conical section and a cylindrical section and shall be manufactured with centrifugal cast technology.  The bowl consists of maximum two pieces.  The cylindrical part provides the liquid pool and the conical part the so-called beach section. The conical section shall terminate with the solids discharge ports, lined with replaceable bushings to compensate for wear.

The wide end of the bowl (liquid discharge) shall be closed by an end piece with exchangeable liquid overflow weirs which determine the liquid level (pool depth).

The conveyor shall be coaxial journalised in grease lubricated bearings inside the bowl assembly. The leading faces and tips of the scroll conveyor flights shall be wear-protected by wear resistant alloy, designed for 15,000 hours operation in normal service. The condition of the wear protection shall be monitored through drilled holes in the bowl. The feed ports in the scroll shall be protected by exchangeable, hard surfaced bushings.

Bearings shall be designed for 100,000 hours operation. Seals shall be Nitrile rubber.

Electrical Motors shall have at least IP 55 protection class

The foundation shall be a sturdy construction to provide stability, and shall house the centrifuge bearings attached with bolts in the foundation, functioning as motor bracket. The foundation shall be equipped with vibration absorbers. Inlet connector for sludge, water and polymer with a flexible hose to connect to the sludge pipeline, rejects outlet hose and sludge cake outlet box.

Materials of Construction shall be as per the following:

- Foundation:	 		min. DIN 17100 steel 37.2 and 44.5

- Bowl:		 		min. DIN 1.4462, Duplex (SAF 2205) stainless steel

- Scroll body: 			min. EN 1.4404 (AISI 316L) stainless steel

- Scroll flights: 			min. EN 1.4404 (AISI 316L) stainless steel

- Cover, sludge outlet: 	min. EN 1.4404 (AISI 316L) stainless steel

- Cover, reject outlet	: 	min. EN 1.4404 (AISI 316L) stainless steel

- Motor and bowl cover: min. GG 25 Cast Iron, EN 1.4307 (AISI 304L) or higher

Wear protection:

- Scroll flights Binder	: Tungsten carbide powder coating

- Comer surface			: Tungsten carbide powder coating

- Wear surface 			: Tungsten carbide powder coating

- Sludge outlet ports 		: Exchangeable hardened stainless-steel bushings

- Sludge inlet 			: Exchangeable hardened stainless-steel bushings

- Feed chamber 			: Exchangeable hardened stainless-steel bushings

Alternative materials of construction and wear protection, if proposed, shall be of equal or higher quality than the above specification and shall be subject to approval by the Project Manager.

Vibration: Maximum allowable vibration, at factory test, shall be 3 mm/s.

Noise level: of the decanter-centrifuge shall not exceed 85±2 dB(A).

Provisions shall be taken for the separation of rewash water and the circulation of dewatered sludge into discharge system, in the case that the system is out of circuit. The velocity of centrifuge drive motors shall be convenient to run time of centrifuges.

### Polymer preparation and dosing system

The units shall prepare, dilute and dose a polymer solution prepared from dry polymer powder. The unit shall also be suitable for the dilution and dosing of liquid polymer from polymer drums. The necessary agitators to prepare polymer solution shall be supplied with polymer preparation tanks. Agitator material shall be durable against polymer. The axle and wings shall be of EN 1.4404 (AISI 316L) or better stainless steel.

Powder hoppers shall be filled by means of vacuum conveyors to ensure dust free handling.

Polymer dosing pumps shall be provided with variable capacity and as well as in-line dosing/mixing systems for mixing the influent sludge and polymer shall be included. The dosing pumps shall be of the progressive cavity pump type with maximum rotation speed of 200 rpm. Each pump shall be protected against overload by means of pressure switch on the pressure side of the pump and the pumps shall be furnished with an automatic dry running protection.

Necessary tanks shall be included. The tanks shall be fitted with a low-level switch, a dry running switch for the dosing pump, a pump connection valve and a bottom drain valve.

A valve system shall allow flexibility in the polymer dosing. Hence switching from one polymer dosing unit to the other shall be done by means of valves and each polymer dosing pump shall by change in the valve position supply either of the dewatering lines.

All steel constructions, pipes, etc. in contact with the sludge and reject water shall be made of stainless steel EN 1.4404 (AISI 316L). Polymer pipes shall be accepted as PE pipe.

The polymer unit shall be located and arranged in a way that gives no obstructions for filling with polymer, service and maintenance.

### Sludge Drying Unit

Solar Drying Unit

The Contractor shall furnish, install, and test all the equipment necessary to provide a complete sludge drying system including all ancillary equipment as defined below, capable of producing a granulated and dried product from a mechanically dewatered wastewater sludge.

The dewatered sludge shall be transferred via belt conveyor to solar drying units and distributed to the drying halls automatically by screw conveyors or other automatic methods.

The dewatered sludge shall be dried to get minimum outlet sludge dry solids content of 90%. The drying process shall be solar drying. The solar drying units shall be composed of minimum automated sludge turning/moving equipment and sludge drying hall structures including climate controlled ventilation system, under floor or other heating as specified section 3 if needed.

All process data of the drying system itself and operating information of equipment and instruments to be installed on this system shall be transferred to SCADA system.

The number of sludge drying halls and turning/moving equipment shall be at least 2 no.

Sludge turning and/or moving equipment

- shall be automated and capable of turning and working over the sludge from dewatering facilities.

- shall be adjustable in its working height above the ground.

- shall have a local control panel mounted on the unit to provide manual control for maintenance operation.

- shall be provided with safety features that prevent automatic operation when operators are in the immediate area. An acoustic signal shall activate on start-up and a visual strobe light/beacon shall indicate that the equipment is in service.

The body of sludge turning and/or moving equipment shall be made of epoxy coated or hot dip galvanised steel and the parts contacting the sludge shall be made of stainless steel EN 1.4404.

Ventilation System

- The Sludge Drying Halls shall be provided with a climate-controlled ventilation system which shall include a combination of fans, motorised vents and louvers.

- The control system is to measure as a minimum temperature and humidity within the sludge drying halls and is to include an external weather station which measures temperature, humidity, wind speed, wind direction and rain. The contractor shall provide all of the equipment and instrumentation required to automate the roof vents including control system, electric motors to operate vents and weather station.

- A ventilation system with a high degree of flexibility is required to provide the optimum conditions of temperature and humidity within the structure to achieve the best results for sludge drying.

### Well water supply system

Technical water shall be based on tap water. The one-way flow shall be secured on e.g. a booster pump system including pressure holding tank, pump and check valve.

Technical water applies to all installations that require clean water and were treated wastewater for reuse shall be inapplicable.

### Treated wastewater for reuse supply system

The treated wastewater water for reuse supply system shall be based on usage of treated wastewater from downstream the secondary clarifiers.

The use of treated wastewater for reuse shall comply with current national standards and regulations.

The treated wastewater shall supply water for all installations as detailed Document No 2, Wash water Sytem.

The treated wastewater shall pass an automatic self-cleaning water filter with a mesh applicable to the consuming installations respecting e.g. spray nozzles etc.

The capacity of the treated water system shall meet the total requirements of the plant inclusive requirements for irrigation within the plant area.

The pressure at the various tapping points shall be kept constant by means of a pressure booster unit. As the flow variations are expected to be large and fast the pressure booster unit shall be able to respond equally. Consequently, some of the pumps at the pressure booster unit shall be regulated by frequency converters.

The self-cleaning filter shall be designed to prevent all possible nozzles, control valves etc from clogging. The self-cleaning filter shall be able to run its own cleaning sequence e.g. by a certain differential pressure over the filter. The filter shall be equipped with pressure gauges at both inlet and discharge side.

### Spare parts

The Contractor shall provide all spare parts required for the safe and continuous operation of the complete plant during the performance demonstration period. These parts shall be delivered prior to the final delivery of the Works.

Based on the manufacturer’s recommendations, the Contractor shall prepare a detailed list of the spare parts required for a two-year operational period for all electro-mechanical equipment. This list shall be submitted to the Project Manager for review and acceptance prior to delivery to the Employer and/or End Recipient.

The spare parts shall be complied with the standards and requirements given in item7.1 and the related equipment section.

### Tools

A complete set of tools including spanners and special tools, necessary for the servicing, maintenance and dismantling of most critical parts of all the mechanical equipment shall be handed over by the Contractor immediately before taking-over. The Contractor shall, based on the manufacture’s recommendation, determine the required tools for all equipment and prepare a list of tools. The list shall be included in the tender.